STATE BOARD OF HEALTH

REGISTRAR'S NOTICE: The following regulatory action is exempt from the Administrative Process Act in accordance with § 2.2-4006 A 4 c of the Code of Virginia, which excludes regulations that are necessary to meet the requirements of federal law or regulations provided such regulations do not differ materially from those required by federal law or regulation. The Department of Health will receive, consider and respond to petitions by any interested person at any time with respect to reconsideration or revision.

Title of Regulation: 12 VAC 5-590. Waterworks Regulations (amending 12 VAC 5-590-10, 12 VAC 5-590-370, 12 VAC 5-590-410, 12 VAC 5-590-420, 12 VAC 5-590-440, 12 VAC 5-590-500, 12 VAC 5-590-530, 12 VAC 5-590-540, and 12 VAC 5-590-550; Appendix B and Appendix F).

Statutory Authority: §§ 32.1-12 and 32.1-170 of the Code of Virginia.

Effective Date: July 3, 2002.

Summary:

The amendments implement higher standards in the treatment of surface water and stricter standards for disinfectants and disinfectant byproducts in drinking water as required by the Environmental Protection Agency. The amendments conform the Virginia Waterworks Regulations to the 1996 amendments to the federal Safe Drinking Water Act.

Agency Contact: Elizabeth Crocker, Department of Health, 1500 East Main Street, Room 109, Richmond, VA 23218, telephone (804) 371-2885.

12 VAC 5-590-10. Definitions.

As used in this chapter, the following words and terms hereinafter set forth shall have meanings respectively set forth unless the context clearly requires a different meaning. :

"Action level" means the concentration of lead or copper in water specified in 12 VAC 5-590-410 E, which determines, in some cases, the treatment requirements contained in 12 VAC 5-590-420 C, D, E and F that a waterworks is required to complete.

"Air gap separation" means the unobstructed vertical distance through the free atmosphere between the lowest opening from any pipe or faucet supplying pure water to a tank, plumbing fixture, or other device and the rim of the receptacle.

"Annual daily water demand" means the average rate of daily water usage over at least the most recent three-year period.

"Applied water" means water that is ready for filtration.

"Approved" means material, equipment, workmanship, process or method that has been accepted by the division as suitable for the proposed use.

"Auxiliary water system" means any water system on or available to the premises other than the waterworks. These auxiliary waters may include water from a source such as wells, lakes, or streams; or process fluids; or used water. They may be polluted or contaminated or objectionable, or constitute an unapproved water source or system over which the water purveyor does not have control.

"Backflow" means the flow of water or other liquids, mixtures, or substances into the distribution piping of a waterworks from any source or sources other than its intended source.

"Backflow prevention device" means any approved device, method, or type of construction intended to prevent backflow into a waterworks.

"Best available technology (BAT)" means the best technology, treatment techniques, or other means which the commissioner finds, after examination for efficacy under field conditions and not solely under laboratory conditions and in conformance with applicable EPA regulations, are available (taking cost into consideration).

"Board" means the State Board of Health.

"Breakpoint chlorination" means the addition of chlorine to water until the chlorine demand has been satisfied and further additions result in a residual that is directly proportional to the amount added.

"Chlorine" means dry chlorine.

"Chlorine gas" means dry chlorine in the gaseous state.

"Chlorine solution (chlorine water)" means a solution of chlorine in water. Note: the term chlorine solution is sometimes used to describe hypochlorite solutions. This use of the term is incorrect.

"Coagulation" means a process using coagulant chemicals and mixing by which colloidal and suspended materials are destabilized and agglomerated into flocs.

"Coliform bacteria group" means a group of bacteria predominantly inhabiting the intestines of man or animal but also occasionally found elsewhere. It includes all aerobic and facultative anaerobic, gram-negative, non-sporeforming bacilli that ferment lactose with production of gas. Also included are all bacteria that produce a dark, purplish-green colony with metallic sheen by the membrane filter technique used for coliform identification.

"Commissioner" means the State Health Commissioner.

"Community water system" means a waterworks which serves at least 15 service connections used by year-round residents or regularly serves at least 25 year-round residents.

"Compliance cycle" means the nine-year calendar year cycle during which a waterworks must monitor. Each compliance cycle consists of three three-year compliance periods. The first calendar year cycle begins January 1, 1993, and ends December 31, 2001; the second begins January 1, 2002, and ends December 31, 2010; the third begins January 1, 2011, and ends December 31, 2019.

"Compliance period" means a three-year calendar year period within a compliance cycle. Each compliance cycle has three three-year compliance periods. Within the first compliance cycle, the first compliance period runs from January 1, 1993, to December 31, 1995; the second from January 1, 1996, to December 31, 1998; the third from January 1, 1999, to December 31, 2001.

“Comprehensive performance evaluation” (CPE) is a thorough review and analysis of a treatment plant's performance-based capabilities and associated administrative, operational and maintenance practices. It is conducted to identify factors that may be adversely impacting a plant's capability to achieve compliance and emphasizes approaches that can be implemented without significant capital improvements. For purposes of compliance with 12 VAC 5-590-530 C 1 b (2) (d), the comprehensive performance evaluation must consist of at least the following components: assessment of plant performance; evaluation of major unit processes; identification and prioritization of performance limiting factors; assessment of the applicability of comprehensive technical assistance; and preparation of a CPE report.

"Confluent growth" means a continuous bacterial growth covering the entire filtration area of a membrane filter, or a portion thereof, in which bacterial colonies are not discrete.

"Consecutive waterworks" means a waterworks which has no water production or source facility of its own and which obtains all of its water from another permitted waterworks.

"Consumer" means any person who drinks water from a waterworks.

"Consumer's water system" means any water system located on the consumer's premises, supplied by or in any manner connected to a waterworks.

"Contaminant" means any objectionable or hazardous physical, chemical, biological, or radiological substance or matter in water.

"Conventional filtration treatment" means a series of processes including coagulation, flocculation, sedimentation, and filtration resulting in substantial particulate removal.

"Corrosion inhibitor" means a substance capable of reducing the corrosivity of water toward metal plumbing materials, especially lead and copper, by forming a protective film on the interior surface of those materials.

"Cross connection" means any connection or structural arrangement, direct or indirect, to the waterworks whereby backflow can occur.

"CT" or "CTcalc" means the product of "residual disinfectant concentration" (C) in mg/L determined before or at the first customer, and the corresponding "disinfectant contact time" (T) in minutes, i.e., "C" x "T."

"Daily fluid intake" means the daily intake of water for drinking and culinary use and is defined as two liters.

"Dechlorination" means the partial or complete reduction of residual chlorine in water by any chemical or physical process at a waterworks with a treatment facility.

"Degree of hazard" means the level of health hazard, as derived from an evaluation of the potential risk to health and the adverse effect upon the waterworks.

"Diatomaceous earth filtration" means a process resulting in substantial particulate removal in which (i) a precoat cake of diatomaceous earth filter media is deposited on a support membrane (septum), and (ii) while the water is filtered by passing through the cake on the septum, additional filter media known as body feed is continuously added to the feed water to maintain the permeability of the filter cake.

"Direct filtration" means a series of processes including coagulation and filtration but excluding sedimentation resulting in substantial particulate removal.

"Disinfectant" means any oxidant (including chlorine) that is added to water in any part of the treatment or distribution process for the purpose of killing or deactivating pathogenic organisms.

"Disinfectant contact time ("T" in CT calculations)" means the time in minutes that it takes for water to move from the point of disinfectant application to the point where residual disinfectant concentration ("C") is measured.

"Disinfection" means a process which inactivates pathogenic organisms in water by chemical oxidants or equivalent agents.

"Disinfection profile" means a summary of daily Giardia lamblia inactivation through the treatment plant.

"Distribution main" means a water main whose primary purpose is to provide treated water to service connections.

"Division" means the Commonwealth of Virginia, Department of Health, Division of Drinking Water Supply Engineering.

"Domestic or other nondistribution system plumbing problem" means a coliform contamination problem in a waterworks with more than one service connection that is limited to the specific service connection from which the coliform positive sample was taken.

"Domestic use or usage" means normal family or household use, including drinking, laundering, bathing, cooking, heating, cleaning and flushing toilets (see Article 2 (§ 32.1-167 et seq.) of Chapter 6 of Title 32.1 of the Code of Virginia).

"Double gate-double check valve assembly" means an approved assembly composed of two single independently acting check valves including tightly closing shutoff valves located at each end of the assembly and petcocks and test gauges for testing the watertightness of each check valve.

"Effective corrosion inhibitor residual," for the purpose of 12 VAC 5-590-420 C 1 only, means a concentration sufficient to form a passivating film on the interior walls of a pipe.

"Enhanced coagulation" means the addition of sufficient coagulant for improved removal of disinfection byproduct precursors by conventional filtration treatment.

"Enhanced softening" means the improved removal of disinfection byproduct precursors by precipitative softening.

"Entry point" means the place where water from the source after application of any treatment is delivered to the distribution system.

"Equivalent residential connection" means a volume of water used equal to a residential connection which is 400 gallons per day unless supportive data indicates otherwise.

"Exception" means an approved deviation from a "shall" criteria contained in Part III of this chapter.

"Exemption" means a conditional waiver of a specific PMCL or treatment technique requirement which is granted to a specific waterworks for a limited period of time.

"Filter profile" means a graphical representation of individual filter performance, based on continuous turbidity measurements or total particle counts versus time for an entire filter run, from startup to backwash inclusively, that includes an assessment of filter performance while another filter is being backwashed.

"Filtration" means a process for removing particulate matter from water by passage through porous media.

"First draw sample" means a one-liter sample of tap water, collected in accordance with 12 VAC 5-590-370 B 6 a (2), that has been standing in plumbing pipes at least six hours and is collected without flushing the tap.

"Flocculation" means a process to enhance agglomeration or collection of smaller floc particles into larger, more easily settleable particles through gentle stirring by hydraulic or mechanical means.

"Free available chlorine" means that portion of the total residual chlorine remaining in water at the end of a specified contact period which will react chemically and biologically as hypochlorous acid or hypochlorite ion.

"GAC10" means granular activated carbon filter beds with an empty-bed contact time of 10 minutes based on average daily flow and a carbon reactivation frequency of every 180 days.

"Governmental entity" means the Commonwealth, a town, city, county, service authority, sanitary district or any other governmental body established under the Code of Virginia, including departments, divisions, boards or commissions.

"Gross alpha particle activity" means the total radioactivity due to alpha particle emission as inferred from measurements on a dry sample.

"Gross beta particle activity" means the total radioactivity due to beta particle emission as inferred from measurements on a dry sample.

"Groundwater" means all water obtained from sources not classified as surface water (or surface water sources).

"Groundwater under the direct influence of surface water" means any water beneath the surface of the ground with (i) significant occurrence of insects or other macroorganisms, algae, or large-diameter pathogens such as Giardia lamblia, or (ii) Cryptosporidium. It also means significant and relatively rapid shifts in water characteristics such as turbidity, temperature, conductivity, or pH which that closely correlate to climatological or surface water conditions. The pathogen, Cryptosporidium, applies to all waterworks that use surface water or groundwater under the direct influence of surface water will be determined by serving at least 10,000 people. The division in accordance with 12 VAC 5-590-430 will determine direct influence of surface water.

"Haloacetic acids (five)" or "(HAA5)" means the sum of the concentrations in milligrams per liter of the haloacetic acid compounds (monochloroacetic acid, dichloroacetic acid, trichloroacetic acid, monobromoacetic acid, and dibromoacetic acid), rounded to two significant figures after addition.

"Halogen" means one of the chemical elements chlorine, bromine, fluorine, astatine or iodine.

"Health hazard" means any condition, device, or practice in a waterworks or its operation that creates, or may create, a danger to the health and well-being of the water consumer.

"Health regulations" means regulations which include all primary maximum contaminant levels, treatment technique requirements, and all operational regulations, the violation of which would jeopardize the public health.

"Hypochlorite" means a solution of water and some form of chlorine, usually sodium hypochlorite.

"Initial compliance period" means for all regulated contaminants, the initial compliance period is the first full three-year compliance period beginning at least 18 months after promulgation with the exception of waterworks with 150 or more service connections for contaminants listed at Table 2.3, VOC 19-21; Table 2.3, SOC 19-33; and antimony, beryllium, cyanide (as free cyanide), nickel, and thallium which shall begin January 1993.

"Interchangeable connection" means an arrangement or device that will allow alternate but not simultaneous use of two sources of water.

"Karstian geology" means an area predominantly underlain by limestone, dolomite, or gypsum and characterized by rapid underground drainage. Such areas often feature sinkholes, caverns, and sinking or disappearing creeks. In Virginia, this generally includes all that area west of the Blue Ridge and, in Southwest Virginia, east of the Cumberland Plateau.

"Large waterworks," for the purposes of 12 VAC 5-590-370 B 6, 12 VAC 5-590-420 C through F, 12 VAC 5-590-530 D, and 12 VAC 5-590-550 D only, means a waterworks that serves more than 50,000 persons.

"Lead service line" means a service line made of lead which connects the water main to the building inlet and any lead pigtail, gooseneck or other fitting which is connected to such lead line.

"Legionella" means a genus of bacteria, some species of which have caused a type of pneumonia called Legionnaires Disease.

"Liquid chlorine" means a liquefied, compressed gas as shipped in commerce. Note: The term liquid chlorine is sometimes used to describe a hypochlorite solution often employed for swimming pool sanitation. This use of the term is incorrect.

"Log inactivation (log removal)" means that a 99.9% reduction is a 3-log inactivation; a 99.99% reduction is a 4-log inactivation.

"Man-made beta particle and photon emitters" means all radionuclides emitting beta particles and/or photons listed in the most current edition of "Maximum Permissible Body Burdens and Maximum Permissible Concentration of Radionuclides in Air or Water for Occupational Exposure," National Bureau of Standards Handbook 69, except the daughter products of thorium-232, uranium-235 and uranium-238.

"Maximum daily water demand" means the rate of water usage during the day of maximum water use.

"Maximum contaminant level (MCL)" means the maximum permissible level of a contaminant in water which is delivered to any user of a waterworks, except in the cases of turbidity and VOCs, where the maximum permissible level is measured at each entry point to the distribution system. Contaminants added to the water under circumstances controlled by the user, except those resulting from corrosion of piping and plumbing caused by water quality, are excluded from this definition. Maximum contaminant levels may be either "primary" (PMCL), meaning based on health considerations or "secondary" (SMCL) meaning based on aesthetic considerations.

"Maximum residual disinfectant level (MRDL)" means a level of a disinfectant added for water treatment that may not be exceeded at the consumer's tap without an unacceptable possibility of adverse health effects. For chlorine and chloramines, a waterworks is in compliance with the MRDL when the running annual average of monthly averages of samples taken in the distribution system, computed quarterly, is less than or equal to the MRDL. For chlorine dioxide, a waterworks is in compliance with the MRDL when daily samples are taken at the entrance to the distribution system and no two consecutive daily samples exceed the MRDL. MRDLs are enforceable in the same manner as maximum contaminant levels. There is convincing evidence that addition of a disinfectant is necessary for control of waterborne microbial contaminants. Notwithstanding the MRDLs listed in Table 2.12, operators may increase residual disinfectant levels of chlorine or chloramines (but not chlorine dioxide) in the distribution system to a level and for a time necessary to protect public health to address specific microbiological contamination problems caused by circumstances such as distribution line breaks, storm runoff events, source water contamination, or cross-connections.

“Maximum residual disinfectant level goal (MRDLG)" means the maximum level of a disinfectant added for water treatment at which no known or anticipated adverse effect on the health of persons would occur, and which allows an adequate margin of safety. MRDLGs are nonenforceable health goals and do not reflect the benefit of the addition of the chemical for control of waterborne microbial contaminants.

"Maximum total trihalomethane potential (MTP)" means the maximum concentration of total trihalomethanes produced in a given water containing a disinfectant residual after seven days at a temperature of 25°C or above.

"Medium-size waterworks," for the purpose of 12 VAC 5-590-370 B 6, 12 VAC 5-590-420 C through F, 12 VAC 5-590-530, and 12 VAC 5-590-550 D only, means a waterworks that serves greater than 3,300 and less than or equal to 50,000 persons.

"Most probable number (MPN)" means that number of organisms per unit volume that, in accordance with statistical theory, would be more likely than any other number to yield the observed test result or that would yield the observed test result with the greatest frequency, expressed as density of organisms per 100 milliliters. Results are computed from the number of positive findings of coliform-group organisms resulting from multiple-portion decimal-dilution plantings.

"Noncommunity water system" means a waterworks that is not a community waterworks, but operates at least 60 days out of the year.

"Nonpotable water" means water not classified as pure water.

"Nontransient noncommunity water system (NTNC)" means a waterworks that is not a community waterworks and that regularly serves at least 25 of the same persons over six months out of the year.

"One hundred (100) year flood level" means the flood elevation which will, over a long period of time, be equaled or exceeded on the average once every 100 years.

"Operator" means any individual employed or appointed by any owner, and who is designated by such owner to be the person in responsible charge, such as a supervisor, a shift operator, or a substitute in charge, and whose duties include testing or evaluation to control waterworks operations. Not included in this definition are superintendents or directors of public works, city engineers, or other municipal or industrial officials whose duties do not include the actual operation or direct supervision of waterworks.

"Optimal corrosion control treatment" means the corrosion control treatment that minimizes the lead and copper concentrations at users' taps while ensuring that the treatment does not cause the waterworks to violate any other section of this chapter.

"Owner" or "water purveyor" means an individual, group of individuals, partnership, firm, association, institution, corporation, governmental entity, or the federal government which supplies or proposes to supply water to any person within this state from or by means of any waterworks (see Article 2 (§ 32.1-167 et seq.) of Chapter 6 of Title 32.1 of the Code of Virginia).

"Picocurie (pCi)" means that quantity of radioactive material producing 2.22 nuclear transformations per minute.

"Point of disinfectant application" means the point where the disinfectant is applied and water downstream of that point is not subject to recontamination by surface water runoff.

"Point-of-entry treatment device (POE)" means a treatment device applied to the water entering a house or building for the purpose of reducing contaminants in the water distributed throughout the house or building.

"Point-of-use treatment device (POU)" means a treatment device applied to a single tap for the purpose of reducing contaminants in the water at that one tap.

"Pollution" means the presence of any foreign substance (chemical, physical, radiological, or biological) in water that tends to degrade its quality so as to constitute an unnecessary risk or impair the usefulness of the water.

"Pollution hazard" means a condition through which an aesthetically objectionable or degrading material may enter the waterworks or a consumer's water system.

"Post-chlorination" means the application of chlorine to water subsequent to treatment.

"Practical quantitation level (PQL)" means the lowest level achievable by good laboratories within specified limits during routine laboratory operating conditions.

"Prechlorination" means the application of chlorine to water prior to filtration.

"Process fluids" means any fluid or solution which may be chemically, biologically, or otherwise contaminated or polluted which would constitute a health, pollutional, or system hazard if introduced into the waterworks. This includes, but is not limited to:

1. Polluted or contaminated water,

2. Process waters,

3. Used waters, originating from the waterworks which may have deteriorated in sanitary quality,

4. Cooling waters,

5. Contaminated natural waters taken from wells, lakes, streams, or irrigation systems,

6. Chemicals in solution or suspension, and

7. Oils, gases, acids, alkalis, and other liquid and gaseous fluid used in industrial or other processes, or for fire fighting purposes.

"Pure water" or "potable water" means water fit for human consumption and domestic use which is sanitary and normally free of minerals, organic substances, and toxic agents in excess of reasonable amounts for domestic usage in the area served and normally adequate in quantity and quality for the minimum health requirements of the persons served (see Article 2 (§ 32.1-167 et seq.) of Chapter 6 of Title 32.1 of the Code of Virginia).

"Raw water main" means a water main which conveys untreated water from a source to a treatment facility.

"Reduced pressure principle backflow prevention device (RPZ device)" means a device containing a minimum of two independently acting check valves together with an automatically operated pressure differential relief valve located between the two check valves. During normal flow and at the cessation of normal flow, the pressure between these two checks shall be less than the supply pressure. In case of leakage of either check valve, the differential relief valve, by discharging to the atmosphere, shall operate to maintain the pressure between the check valves at less than the supply pressure. The unit must include tightly closing shut-off valves located at each end of the device, and each device shall be fitted with properly located test cocks. These devices must be of the approved type.

"REM" means the unit of dose equivalent from ionizing radiation to the total body or any internal organ or organ system. A "millirem" (MREM) is 1/1000 of a REM.

"Repeat compliance period" means any subsequent compliance period after the initial compliance period.

"Residual disinfectant concentration ("C" in CT Calculations)" means the concentration of disinfectant measured in mg/L in a representative sample of water.

"Responsible charge" means designation by the owner of any individual to have duty and authority to operate or modify the operation of waterworks processes.

"Sanitary facilities" means piping and fixtures, such as sinks, lavatories, showers, and toilets, supplied with potable water and drained by wastewater piping.

"Sanitary survey" means an investigation of any condition that may affect public health.

"Secondary water source" means any approved water source, other than a waterworks' primary source, connected to or available to that waterworks for emergency or other nonregular use.

"Sedimentation" means a process for removal of solids before filtration by gravity or separation.

"Service connection" means the point of delivery of water to a customer's building service line as follows:

1. If a meter is installed, the service connection is the downstream side of the meter;

2. If a meter is not installed, the service connection is the point of connection to the waterworks;

3. When the water purveyor is also the building owner, the service connection is the entry point to the building.

"Service line sample" means a one-liter sample of water, collected in accordance with 12 VAC 5-590-370 B 6 a (2) (c), that has been standing for at least six hours in a service line.

"Sewer" means any pipe or conduit used to convey sewage or industrial waste streams.

"Single family structure," or the purpose of 12 VAC 5-590-370 B 6 (a) only, means a building constructed as a single-family residence that is currently used as either a residence or a place of business.

"Slow sand filtration" means a process involving passage of raw water through a bed of sand at low velocity (generally less than 0.4 m/h) resulting in substantial particulate removal by physical and biological mechanisms.

"Small waterworks," for the purpose of 12 VAC 5-590-370 B 6, 12 VAC 5-590-420 C through F, 12 VAC 5-590-530 D and 12 VAC 5-590-550 D only, means a waterworks that serves 3,300 persons or fewer.

"Standard sample" means that portion of finished drinking water that is examined for the presence of coliform bacteria.

"Surface water" means all water open to the atmosphere and subject to surface runoff.

“SUVA” means specific ultraviolet absorption at 254 nanometers (nm), an indicator of the humic content of water. It is a calculated parameter obtained by dividing a sample's ultraviolet absorption at a wavelength of 254 nm (UV254) (in m-1) by its concentration of dissolved organic carbon (DOC) (in mg/L).

"Synthetic organic chemicals (SOC)" means one of the family of organic man-made compounds generally utilized for agriculture or industrial purposes.

"System hazard" means a condition posing an actual, or threat of, damage to the physical properties of the waterworks or a consumer's water system.

"Terminal reservoir" means an impoundment providing end storage of water prior to treatment.

"Too numerous to count" means that the total number of bacterial colonies exceeds 200 on a 47-mm diameter membrane filter used for coliform detection.

"Total effective storage volume" means the volume available to store water in distribution reservoirs measured as the difference between the reservoir's overflow elevation and the minimum storage elevation. The minimum storage elevation is that elevation of water in the reservoir that can provide a minimum pressure of 20 psi at a flow as determined in 12 VAC 5-590-690 C to the highest elevation served within that reservoir's service area under systemwide maximum daily water demand.

“Total organic carbon” (TOC) means total organic carbon in mg/L measured using heat, oxygen, ultraviolet irradiation, chemical oxidants, or combinations of these oxidants that convert organic carbon to carbon dioxide, rounded to two significant figures.

"Total trihalomethanes (TTHM)" means the sum of the concentrations of the trihalomethanes expressed in milligrams per liter (mg/L) and rounded to two significant figures. For the purpose of these regulations, the TTHM's shall mean trichloromethane (chloroform), dibromochloromethane, bromodichloromethane, and tribromomethane (bromoform).

"Transmission main" means a water main whose primary purpose is to move significant quantities of treated water among service areas.

"Treatment technique requirement" means a requirement which specifies for a contaminant a specific treatment technique(s) demonstrated to the satisfaction of the division to lead to a reduction in the level of such contaminant sufficient to comply with these regulations.

"Trihalomethane (THM)" means one of the family of organic compounds, named as derivatives of methane, wherein three of the four hydrogen atoms in methane are each substituted by a halogen atom in the molecular structure.

“Uncovered finished water storage facility” is a tank, reservoir, or other facility used to store water that will undergo no further treatment (except residual disinfection) and is open to the atmosphere.

"Unregulated contaminant (UC)" means a contaminant for which a monitoring requirement has been established, but for which no MCL or treatment technique requirement has been estblished established.

"Used water" means any water supplied by a water purveyor from the waterworks to a consumer's water system after it has passed through the service connection.

"Virus" means a virus of fecal origin which is infectious to humans by waterborne transmission.

"Variance" means a conditional waiver of a specific regulation which is granted to a specific waterworks. A PMCL Variance is a variance to a Primary Maximum Contaminant Level, or a treatment technique requirement. An Operational Variance is a variance to an operational regulation or a Secondary Maximum Contaminant Level. Variances for monitoring, reporting and public notification requirements will not be granted.

"Volatile synthetic organic chemical (VOC)" means one of the family of manmade organic compounds generally characterized by low molecular weight and rapid vaporization at relatively low temperatures or pressures.

"Waterborne disease outbreak" means the significant occurrence of acute infectious illness, epidemiologically associated with the ingestion of water from a waterworks which is deficient in treatment, as determined by the commissioner or the State Epidemiologist.

"Water purveyor" (same as owner).

"Water supply" means water that shall have been taken into a waterworks from all wells, streams, springs, lakes, and other bodies of surface waters (natural or impounded), and the tributaries thereto, and all impounded groundwater, but the term "water supply" shall not include any waters above the point of intake of such waterworks (see Article 2 (§ 32.1-167 et seq.) of Chapter 6 of Title 32.1 of the Code of Virginia).

"Water supply main" or "main" means any water supply pipeline that is part of a waterworks distribution system.

"Water Well Completion Report" means a report form published by the State Water Control Board entitled "Water Well Completion Report" which requests specific information pertaining to the ownership, driller, location, geological formations penetrated, water quantity and quality encountered as well as construction of water wells. The form is to be completed by the well driller.

"Waterworks" means a system that serves piped water for drinking or domestic use to (i) the public, (ii) at least 15 connections, or (iii) an average of 25 individuals for at least 60 days out of the year. The term "waterworks" shall include all structures, equipment and appurtenances used in the storage, collection, purification, treatment and distribution of pure water except the piping and fixtures inside the building where such water is delivered (see Article 2 (§ 32.1-167 et seq.) of Chapter 6 of Title 32.1 of the Code of Virginia).

"Waterworks with a single service connection" means a waterworks which supplies drinking water to consumers via a single service line.

12 VAC 5-590-370. Sampling frequency.

The commissioner may exempt consecutive waterworks that obtain potable water from another water system for distribution from all monitoring requirements in this section except for bacteriological (subsection A of this section), trihalomethanes disinfectant residuals, byproducts and disinfection byproduct precursors (subdivision B 3 of this section), and lead and copper (subdivision B 6 of this section). The required sampling frequencies are as follows:

REGISTRAR'S NOTICE: There are no changes to subsection A or subdivisions B 1 or B 2 of this section. Due to their length, these portions of the text are not set out.

B. …

3. Trihalomethanes Disinfectant residuals, disinfection byproducts and disinfection byproduct precursors.

a. The requirements in subdivisions B 3 a (1) through (10) (e) of this section apply to community or nontransient noncommunity waterworks that use a surface water or a groundwater under the direct influence of surface water and serve a population of 10,000 or more until December 31, 2001. The requirements in subdivisions B 3 a (1) through (10) (e) of this section apply to community waterworks that use only groundwater not under the direct influence of surface water that add a disinfectant (oxidant) in any part of the treatment process and serve a population of 10,000 or more until December 31, 2003. After December 31, 2003, subdivisions B 3 a (1) through (10) (e) of this section are no longer applicable.

(1) Samples for TTHM analyses shall be collected quarterly from all community and nontransient noncommunity waterworks which disinfect and serve 10,000 or more individuals. At least four samples for each treatment plant used by the waterworks must be collected using the following criteria: at least 25% of the samples shall be taken at locations within the distribution system reflecting the maximum residence time of the water in the system. The remaining 75% shall be taken at representative locations in the distribution system, taking into account the number of persons served, different sources of water and different treatment methods employed. Sample locations shall be approved by the commissioner.

a. (2) Community and nontransient noncommunity waterworks utilizing surface water in whole or in part, may, upon written request, have the monitoring frequency reduced by the division to a minimum of one sample per quarter taken at a point of maximum residence time of the water in the distribution system. The division must make a written determination that data from at least one year of monitoring and local conditions indicate that TTHM concentrations will be consistently below the PMCL.

If at any time in the reduced monitoring program the results from any analysis exceed the PMCL for TTHMs and such results are confirmed by at least one check sample taken promptly after such results are received, or if the waterworks makes any significant change to its source of water or treatment program, the waterworks shall immediately begin monitoring in accordance with subdivision B 3 of this section. Routine monitoring must continue for at least one year before a reduced monitoring frequency can be implemented again.

b. (3) Community and nontransient noncommunity waterworks utilizing groundwaters only may, upon written request, have the monitoring frequency reduced to a minimum of one sample per year for TTHM. This sample shall be collected at a point in the distribution system reflecting the maximum residence time of the water. The division must make a written determination that the data indicates the system has a TTHM concentration of less than the PMCL and local conditions indicate that TTHM concentrations will be consistently below the PMCL.

If at any time in the reduced monitoring program the results from any TTHM exceed or equal the PMCL and such results are confirmed by at least one check sample taken promptly after such results are received, the waterworks shall immediately begin monitoring in accordance with subdivision B 3 of this section. Routine monitoring must continue for at least one year before a reduced monitoring frequency can be implemented again.

If any significant change occurs in the raw water or if the waterworks treatment process is altered, an additional sample for TTHM shall be analyzed immediately to determine whether the waterworks must comply with the monitoring requirements of subdivision B 3 of this section. The sample shall be collected at a point in the distribution system reflecting the maximum residence time of the water.

c. (4) Nothing shall prevent the division from requiring additional samples for TTHM or MTP analysis when conditions warrant.

d. (5) Nothing shall prevent the TTHM regulations from being applicable to waterworks serving less than 10,000 individuals when in the determination of the division, public health will be better served.

e. (6) With prior approval of the division, waterworks which utilize multiple wells from a common aquifer may consider these multiple sources as one treatment plant for determining the minimum number of samples to be collected for TTHM analysis.

f. (7) All samples for TTHM or MTP taken within an established frequency shall be collected within a 24-hour period.

g. (8) The results of all analyses per quarter shall be arithmetically averaged and reported to the division within 30 days of the owner's receipt of the results (when samples are not analyzed by the state). All samples collected shall be used in the computation of the average unless the results are invalidated for technical reasons.

h. (9) Analysis shall be conducted in accordance with 12 VAC 5-590-440.

i. (10) Before any modification to a waterworks is undertaken for the purposes of complying with this section, approval must be obtained in accordance with 12 VAC 5-590-200. In addition, the following information, as a minimum, may be required from the owner:

(1) (a) An evaluation of the waterworks for sanitary defects and an evaluation of the source water for biological quality;

(2) (b) Evaluation of existing treatment practices and indication of how proposed improvements will minimize disinfectant demand and optimize finished water quality;

(3) (c) Provision of results of a baseline water quality survey. Parameters monitored should include coliform, fecal coliform, fecal streptococci, heterotrophic plate counts at 20°C and 35°C, phosphate, ammonia nitrogen and TOC. Virus studies may be necessary as determined by the division;

(4) (d) Performance of additional monitoring to assure continued maintenance of optimal biological quality in the finished water;

(5) (e) Consideration of a plan to maintain an active disinfectant residual throughout the distribution system at all times during and after proposed modifications.

b. Unless otherwise noted, all waterworks that use a chemical disinfectant must comply with the requirements of this section as follows:

(1) Community or nontransient noncommunity waterworks that use surface water or groundwater under the direct influence of surface water and serving 10,000 or more persons, must comply with this section beginning January 1, 2002.

(2) Community or nontransient noncommunity waterworks that use surface water or groundwater under the direct influence of surface water serving fewer than 10,000 persons and waterworks using only groundwater not under the direct influence of surface water must comply with this section beginning January 1, 2004.

(3) Transient noncommunity waterworks which use surface water or groundwater under the direct influence of surface water and serving 10,000 or more persons and using chlorine dioxide as a disinfectant or oxidant must comply with any requirements for chlorine dioxide in this section beginning January 1, 2002.

(4) Transient noncommunity waterworks which use surface water or groundwater under the direct influence of surface water serving fewer than 10,000 persons and using chlorine dioxide as a disinfectant or oxidant and waterworks using only groundwater not under the direct influence of surface water and using chlorine dioxide as a disinfectant or oxidant must comply with any requirements for chlorine dioxide in this section beginning January 1, 2004.

c. Waterworks must take all samples during normal operating conditions.

(1) Analysis under this section for disinfection byproducts (TTHM, HAA5 and bromate) must be conducted by a laboratory that has received certification by EPA or the state.

(2) Measurement under this section of daily chlorite samples at the entry point to the distribution system, disinfection residuals (free chlorine, combined chlorine, total chlorine and chlorine dioxide), alkalinity, bromide, TOC, SUVA (DOC and UV254), and pH must be made by a party approved by the commissioner.

(3) DPD colorimetric test kits may be used to measure residual disinfectant concentrations for chlorine, chloramines and chlorine dioxide.

d. Failure to monitor in accordance with the monitoring plan required under subdivision B 3 k of this section is a monitoring violation. Failure to monitor will be treated as a violation for the entire period covered by the annual average where compliance is based on a running annual average of monthly or quarterly samples or averages and the waterworks’ failure to monitor makes it impossible to determine compliance with PMCLs or MRDLs.

e. Waterworks may use only data collected under the provisions of this section or the US EPA Information Collection Rule, 40 CFR 141 Subpart M, Information Collection Requirements (ICR) for Public Water Systems, to qualify for reduced monitoring.

f. TTHM/HAA5 monitoring. Community or nontransient noncommunity waterworks must monitor TTHM and HAA5 at the frequency indicated below:

(1) Routine monitoring requirements.

(a) Waterworks using surface water or groundwater under the direct influence of surface water and serving at least 10,000 persons must collect four water samples per quarter per treatment plant. At least 25% of all samples collected each quarter must be at locations representing maximum residence time in the distribution system. The remaining samples must be taken at locations representative of at least average residence time in the distribution system and representative of the entire distribution system. When setting the sample locations the waterworks must take into account number of persons served, different sources of water, and different treatment methods.

(b) Waterworks using surface water or groundwater under the direct influence of surface water and serving from 500 to 9,999 persons must collect one sample per quarter per treatment plant. The sample location must represent maximum residence time in the distribution system.

(c) Waterworks using surface water or groundwater under the direct influence of surface water and serving fewer than 500 persons must collect one sample per year per treatment plant during the month of warmest water temperature. The sample location must represent maximum residence time in the distribution system. If the sample (or average of annual samples, if more than one sample is taken) exceeds PMCL in Table 2.13, the waterworks must increase monitoring to one sample per treatment plant per quarter, taken at a point reflecting the maximum residence time in the distribution system, until waterworks meets reduced monitoring criteria.

(d) Waterworks using only groundwater not under direct influence of surface water using chemical disinfectant and serving at least 10,000 persons must collect one sample per quarter per treatment plant. The sample location must represent maximum residence time in the distribution system.

(e) Waterworks using only groundwater not under direct influence of surface water using chemical disinfectant and serving fewer than 10,000 persons must collect one sample per year per treatment plant during the month of warmest water temperature. The sample location must represent maximum residence time in the distribution system. If the sample (or average of annual samples, if more than one sample is taken) exceeds PMCL in Table 2.13, the waterworks must increase monitoring to one sample per treatment plant per quarter, taken at a point reflecting the maximum residence time in the distribution system, until the waterworks meets the criteria for reduced monitoring found in subdivision B 3 f (4) of this section.

(f) If a waterworks elects to sample more frequently than the minimum required, at least 25% of all samples collected each quarter (including those taken in excess of the required frequency) must be taken at locations that represent the maximum residence time of the water in the distribution system. The remaining samples must be taken at locations representative of at least average residence time in the distribution system.

(g) With prior approval of the commissioner, waterworks that utilize multiple wells from a common aquifer may consider these multiple sources as one treatment plant for determining the minimum number of samples to be collected for TTHM and HAA5 analysis.

(2) After one year of routine monitoring a waterworks may reduce monitoring, except as otherwise provided, as follows:

(a) Waterworks using surface water or groundwater under the direct influence of surface water and serving at least 10,000 persons that has a source water annual average TOC level, before any treatment, of equal to or less than 4.0 mg/L and a TTHM annual average equal to or less than 0.040 mg/L and HAA5 annual average equal to or less than 0.030 mg/L may reduce its monitoring to one sample per treatment plant per quarter at a distribution system location reflecting maximum residence time.

(b) Waterworks using surface water or groundwater under the direct influence of surface water serving from 500 to 9,999 persons that has a source water annual average TOC level, before any treatment of, equal to or less than 4.0 mg/L and a TTHM annual average equal to or less than 0.040 mg/L and HAA5 annual average equal to or less than 0.030 mg/L may reduce its monitoring to one sample per treatment plant per year at a distribution system location reflecting maximum residence time during the month of warmest water temperature.

(c) Waterworks using only groundwater not under the direct influence of surface water, using chemical disinfectant and serving at least 10,000 persons that has a TTHM annual average of equal to or less than 0.040 mg/L and HAA5 annual average of equal to or less than 0.030 mg/L may reduce its monitoring to one sample per treatment plant per year at a distribution system location reflecting maximum residence time during the month of warmest water temperature.

(d) Waterworks using only groundwater not under the direct influence of surface water, using chemical disinfectant and serving fewer than 10,000 persons that has a TTHM annual average equal to or less than 0.040 mg/L and HAA5 annual average equal to or less than 0.030 mg/L for two consecutive years or TTHM annual average equal to or less than 0.020 mg/L and HAA5 annual average of equal to or less than 0.015 mg/L for one year may reduce its monitoring to one sample per treatment plant per three-year monitoring cycle at a distribution system location reflecting maximum residence time during the month of warmest water temperature, with the three-year cycle beginning on January 1 following the quarter in which the system qualifies for reduced monitoring.

(e) Waterworks using surface water or groundwater under the direct influence of surface water serving fewer than 500 persons may not reduce its monitoring to less than one sample per treatment plant per year.

(3) Waterworks on a reduced monitoring schedule may remain on that reduced schedule as long as the average of all samples taken in the year (for waterworks that must monitor quarterly) or the result of the sample (for waterworks that must monitor no more frequently than annually) is no more than 0.060 mg/L and 0.045 mg/L for TTHMs and HAA5, respectively. Waterworks that do not meet these levels must resume monitoring at the frequency identified in subdivision B 3 f (1) of this section in the quarter immediately following the quarter in which the waterworks exceeds 0.060 mg/L or 0.045 mg/L for TTHMs or HAA5, respectively. For waterworks using only groundwater not under the direct influence of surface water and serving fewer than 10,000 persons, if either the TTHMs annual average is greater than 0.080 mg/L or the HAA5 annual average is greater than 0.060 mg/L, the waterworks must go to increased monitoring identified in subdivision B 3 f (1) of this section in the quarter immediately following the monitoring period in which the system exceeds 0.080 mg/L or 0.060 mg/L for TTHM or HAA5 respectively.

(4) Waterworks on increased monitoring may return to routine monitoring if, after at least one year of monitoring, their TTHM annual average is equal to or less than 0.060 mg/L and their HAA5 annual average is equal to or less than 0.045 mg/L.

(5) The commissioner may return a waterworks to routine monitoring at the commissioner’s discretion.

g. Chlorite. Community and nontransient noncommunity waterworks using chlorine dioxide, for disinfection or oxidation, must conduct monitoring for chlorite.

(1) Routine monitoring.

(a) Daily monitoring. Waterworks must take daily samples at the entrance to the distribution system. For any daily sample that exceeds the chlorite PMCL in Table 2.13, the waterworks must take additional samples in the distribution system the following day at the locations required by subdivision B 3 g (1) (c) of this section, in addition to the sample required at the entrance to the distribution system.

(b) Monthly monitoring. Waterworks must take a three-sample set each month in the distribution system. The waterworks must take one sample at each of the following locations: near the first customer, at a location representative of average residence time, and at a location reflecting maximum residence time in the distribution system. Any additional routine sampling must be conducted in the same manner (as three-sample sets, at the specified locations). The waterworks may use the results of additional monitoring conducted under subdivision B 3 g (1) (c) of this section to meet the requirement for monitoring in this paragraph.

(c) Additional monitoring requirements. On each day following a routine sample monitoring result that exceeds the chlorite PMCL in Table 2.13 at the entrance to the distribution system, the waterworks is required to take three chlorite distribution system samples at the following locations: as close to the first customer as possible, in a location representative of average residence time, and as close to the end of the distribution system as possible (reflecting maximum residence time in the distribution system).

(2) Reduced monitoring.

(a) Chlorite monitoring at the entrance to the distribution system required by subdivision B 3 g (1) (a) of this section may not be reduced.

(b) Chlorite monitoring in the distribution system required by subdivision B 3 g (1) (b) of this section may be reduced to one three-sample set per quarter after one year of monitoring where no individual chlorite sample taken in the distribution system under subdivision B 3 g (1) (b) of this section has exceeded the chlorite PMCL in Table 2.13 and the waterworks has not been required to conduct monitoring under subdivision B 3 g (1) (c) of this section. The waterworks may remain on the reduced monitoring schedule until either any of the three individual chlorite samples taken quarterly in the distribution system under subdivision B 3 g (1) (b) of this section exceeds the chlorite PMCL or the waterworks is required to conduct monitoring under subdivision B 3 g (1) (c) of this section, at which time the waterworks must revert to routine monitoring.

h. Bromate.

(1) Each community and nontransient noncommunity waterworks treatment plant using ozone, for disinfection or oxidation, must take one sample per month and analyze it for bromate. Waterworks must take samples monthly at the entrance to the distribution system while the ozonation system is operating under normal conditions.

(2) Waterworks required to analyze for bromate may reduce monitoring from monthly to once per quarter, if the waterworks demonstrates that the average source water bromide concentration is less than 0.05 mg/L based upon representative monthly bromide measurements for one year. The waterworks may remain on reduced bromate monitoring until the running annual average source water bromide concentration, computed quarterly, is equal to or greater than 0.05 mg/L based upon representative monthly measurements. If the running annual average source water bromide concentration is equal to or greater than 0.05 mg/L, the waterworks must resume routine monitoring required by subdivision B 3 h (1) of this section.

(3) Bromide. Waterworks required to analyze for bromate may reduce bromate monitoring from monthly to once per quarter, if the waterworks demonstrates that the average source water bromide concentration is less than 0.05 mg/L based upon representative monthly measurements for one year. The waterworks must continue bromide monitoring to remain on reduced bromate monitoring.

i. Monitoring requirements for disinfectant residuals.

(1) Chlorine and chloramines.

(a) Waterworks that use chlorine or chloramines must measure the residual disinfectant level in the distribution system at the same point in the distribution system and at the same time as total coliforms are sampled, as specified in 12 VAC 5-590-370 A. Waterworks that use surface water or groundwater under the direct influence of surface water may use the results of residual disinfectant concentration sampling found in 12 VAC 5-590-370 B 7 c (1) in lieu of taking separate samples.

(b) Residual disinfectant level monitoring may not be reduced.

(2) Chlorine dioxide.

(a) Waterworks that use chlorine dioxide for disinfection or oxidation must take daily samples at the entrance to the distribution system. For any daily sample that exceeds the MRDL in Table 2.12, the waterworks must take samples in the distribution system the following day at the locations required by subdivision B 3 i (2) (b) of this section, in addition to the sample required at the entrance to the distribution system.

(b) On each day following a routine sample monitoring result that exceeds the MRDL in Table 2.12, the waterworks is required to take three chlorine dioxide distribution system samples. If chlorine dioxide or chloramines are used to maintain a disinfectant residual in the distribution system, or if chlorine is used to maintain a disinfectant residual in the distribution system and there are no disinfection addition points after the entrance to the distribution system (i.e., no booster chlorination), the waterworks must take three samples as close to the first customer as possible, at intervals of at least six hours. If chlorine is used to maintain a disinfectant residual in the distribution system and there are one or more disinfection addition points after the entrance to the distribution system (i.e., booster chlorination), the waterworks must take one sample at each of the following locations: as close to the first customer as possible, in a location representative of average residence time, and as close to the end of the distribution system as possible (reflecting maximum residence time in the distribution system).

(c) Chlorine dioxide monitoring may not be reduced.

j. Monitoring requirements for disinfection byproduct precursors (DBPP).

(1) Community or nontransient noncommunity waterworks using surface water or groundwater under the direct influence of surface water and using conventional filtration treatment (as defined in 12 VAC 5-590-10) must monitor each treatment plant for TOC no later than the point of combined filter effluent turbidity monitoring and representative of the treated water. All waterworks required to monitor under this subdivision (B 3 j (1)) must also monitor for TOC in the source water prior to any treatment at the same time as monitoring for TOC in the treated water. These samples (source water and treated water) are referred to as paired samples. At the same time as the source water sample is taken, all waterworks must monitor for alkalinity in the source water prior to any treatment. Waterworks must take one paired sample and one source water alkalinity sample per month per plant at a time representative of normal operating conditions and influent water quality.

(2) Community or nontransient noncommunity waterworks that use surface water or groundwater under the direct influence of surface water with an average treated water TOC of less than 2.0 mg/L for two consecutive years, or less than 1.0 mg/L for one year, may reduce monitoring for both TOC and alkalinity to one paired sample and one source water alkalinity sample per plant per quarter. The waterworks must revert to routine monitoring in the month following the quarter when the annual average treated water TOC equal to or greater than 2.0 mg/L.

k. Each waterworks required to monitor under subdivision B 3 of this section must develop and implement a monitoring plan. The waterworks must maintain the plan and make it available for inspection by the commissioner and the general public no later than 30 days following the applicable compliance dates in subdivision B 3 b of this section. All community or nontransient noncommunity waterworks that use surface water or groundwater under the direct influence of surface water serving more than 3,300 people must submit a copy of the monitoring plan to the commissioner no later than the date of the first report required under 12 VAC 5-590-530 A. The commissioner may also require the plan to be submitted by any other waterworks. After review, the commissioner may require changes in any plan elements. The plan must include at least the following elements:

(1) Specific locations and schedules for collecting samples for any parameters included in subdivision B 3 of this section.

(2) How the waterworks will calculate compliance with PMCLs, MRDLs, and treatment techniques.

(3) The sampling plan for a consecutive waterworks must reflect the entire consecutive distribution system.

REGISTRAR'S NOTICE: There are no changes to subdivisions B 4 through B 6 of this section. Due to their length, the text for those subdivisions is not set out.

7. Waterworks required to filter Monitoring filtration and disinfection.

a. The owner of a waterworks that uses a surface water source or a groundwater source under the direct influence of surface water and provides filtration treatment must monitor in accordance with this section beginning June 29, 1993, or when filtration is installed, whichever is later.

a. b. Turbidity measurements as required by 12 VAC 5-590-410 C F shall be performed on representative samples of the filtered water every four hours (or more frequently) that the waterworks serves water to the public. A waterworks owner may substitute continuous turbidity monitoring for grab sample monitoring if it validates the continuous measurement for accuracy on a regular basis using a protocol approved by the division. For any waterworks using slow sand filtration or filtration treatment other than conventional treatment, direct filtration, or diatomaceous earth filtration, the division may reduce the sampling frequency to once per day if it determines that less frequent monitoring is sufficient to indicate effective filtration performance. For waterworks serving 500 or fewer persons, the division may reduce the turbidity sampling frequency to once per day, regardless of the type of filtration treatment used, if the division determines that less frequent monitoring is sufficient to indicate effective filtration performance.

(1) In addition to the above, a waterworks serving at least 10,000 people supplied by surface water or groundwater under the direct influence of surface water that provides conventional filtration treatment or direct filtration must conduct continuous monitoring of turbidity for each individual filter, using an approved method in 12 VAC 5-590-440, and must calibrate turbidimeters using the procedure specified by the manufacturer. Waterworks must record the results of individual filter monitoring every 15 minutes.

(2) If there is a failure in the continuous turbidity monitoring equipment, the waterworks must conduct grab sampling every four hours in lieu of continuous monitoring but for no more than five working days following the failure of the equipment.

b. c. The residual disinfectant concentration of the water entering the distribution system shall be monitored continuously, and the lowest value shall be recorded each day, except that if there is a failure in the continuous monitoring equipment, grab sampling every four hours may be conducted in lieu of continuous monitoring, but for no more than five working days following the failure of the equipment, and owners of waterworks serving 3,300 or fewer persons may take grab samples in lieu of continuous monitoring on an ongoing basis at the frequencies each day prescribed below:

| Waterworks size by population | Samples/Day1 |
| --- | --- |
| 500 or less | 1 |
| 501 to 1,000 | 2 |
| 1,000 to 2,500 | 3 |
| 2,501 to 3,300 | 4 |

1The day's samples cannot be taken at the same time. The sampling intervals are subject to commissioner's review and approval.

If at any time the residual disinfectant concentration falls below 0.2 mg/L in a waterworks using grab sampling in lieu of continuous monitoring, the waterworks owner shall take a grab sample every four hours until the residual disinfectant concentration is equal to or greater than 0.2 mg/L.

(1) The residual disinfectant concentration must be measured at least at the same points in the distribution system and at the same time as total coliforms are sampled, as specified in subsection A of this section, except that the division may allow a waterworks owner which uses both a surface water source or a groundwater source under direct influence of surface water, and a groundwater source to take disinfectant residual samples at points other than the total coliform sampling points if the division determines that such points are more representative of treated (disinfected) water quality within the distribution system. Heterotrophic bacteria, measured as heterotrophic plate count (HPC) as specified in 12 VAC 5-590-420 B may be measured in lieu of residual disinfectant concentration.

(2) If the division determines, based on site-specific considerations, that a waterworks has no means for having a sample transported and analyzed for HPC by a certified laboratory under the requisite time and temperature conditions and that the waterworks is providing adequate disinfection in the distribution system, the requirements of subdivision B 7 (1) of this section do not apply to that waterworks.

c. d. The following information on the samples taken in the distribution system in conjunction with total coliform monitoring pursuant to 12 VAC 5-590-420 B shall be reported monthly to the division by the waterworks owner:

(1) Number of instances where the residual disinfectant concentration is measured;

(2) Number of instances where the residual disinfectant concentration is not measured but HPC is measured;

(3) Number of instances where the residual disinfectant concentration is measured but not detected and no HPC is measured;

(4) Number of instances where no residual disinfectant concentration is detected and where the HPC is greater than 500/mL;

(5) Number of instances where the residual disinfectant concentration is not measured and HPC is greater than 500/mL.

(6) For the current and previous month the waterworks serves water to the public, the value of "V" in percent in the following formula:

V = [(c + d + e) / (a + b)] X 100

where

a = the value in subdivision B 7 c d (1) of this section,

b = the value in subdivision B 7 c d (2) of this section,

c = the value in subdivision B 7 c d (3) of this section,

d = the value in subdivision B 7 c d (4) of this section,

e = the value in subdivision B 7 c d (5) of this section,

(7) If the division determines, based on site-specific considerations, that a waterworks owner has no means for having a sample transported and analyzed for HPC by a certified laboratory within the requisite time and temperature conditions and that the waterworks is providing adequate disinfection in the distribution system, the requirements of subdivision B 7 b c (1) of this section do not apply.

d. e. A waterworks owner need not report the data listed in 12 VAC 5-590-530 C 2 a if all data listed in 12 VAC 5-590-530 C 2 a through c remain on file at the waterworks and the division determines that the waterworks owner has submitted all the information required by 12 VAC 5-590-530 C 2 a through c for at least 12 months.

8. Operational. Waterworks owners may be required by the division to collect additional samples to provide quality control for any treatment processes that are employed.

C. Physical. All samples for turbidity analysis shall be taken at a representative entry point or points to the water distribution system unless otherwise specified. Turbidity samples shall be analyzed, at least once per day at all waterworks that use surface water sources or groundwater sources under the direct influence of surface water.

D. Radiological. The frequency of radiological sampling shall be accordance with 12 VAC 5-590-400.

12 VAC 5-590-410. Determination of compliance.

For the purposes of determining compliance with a PMCL or action level, the following criteria shall be used:

A. Bacteriological results. Compliance with the PMCL for coliform bacteria shall be determined as specified in 12 VAC 5-590-380 C. Repeat samples shall be used as a basis for determining compliance with these regulations.

B. Inorganic chemicals.

1. Antimony, asbestos, barium, beryllium, cadmium, cyanide (as free cyanide), chromium, fluoride, mercury, nickel, selenium, and thallium. Where the results of sampling for antimony, asbestos, barium, beryllium, cadmium, cyanide (as free cyanide), chromium, fluoride, mercury, nickel, selenium, or thallium exceed the PMCL, the waterworks shall take a confirmation sample, at the same sampling point, within two weeks of notification of the analytical results of the first sample.

a. The results of the initial and confirmation samples shall be averaged to determine compliance with subdivision 1 c of this subsection. The commissioner has the discretion to delete results of obvious sampling errors.

b. The commissioner may require more frequent monitoring.

c. Compliance with antimony, asbestos, barium, beryllium, cadmium, cyanide (as free cyanide), chromium, fluoride, mercury, nickel, selenium, and thallium in Table 2.2 shall be determined based on the analytical result(s) obtained at each sampling point.

(1) For waterworks which are conducting monitoring more frequently than annually, compliance with the PMCL for antimony, asbestos, barium, beryllium, cadmium, cyanide (as free cyanide), chromium, fluoride, mercury, nickel, selenium, and thallium is determined by a running annual average at each sampling point. If the average at any sampling point is greater than the PMCL, then the waterworks is out of compliance. If any one sample would cause the annual average to be exceeded, then the waterworks is out of compliance immediately. Any sample below the detection limit shall be calculated at zero for the purpose of determining the annual average. (NOTE: Refer to detection definition at 12 VAC 5-590-370 B 2 h.)

(2) For waterworks which are monitoring annually, or less frequently, the waterworks is out of compliance with the PMCL for antimony, asbestos, barium, beryllium, cadmium, cyanide (as free cyanide), chromium, fluoride, mercury, nickel, selenium, and thallium if the average of the original sample and a confirmation sample of a contaminant at any sampling point is greater than the PMCL. However, if the confirmation sample is not collected, the waterworks is in violation of the PMCL for antimony, asbestos, barium, beryllium, cadmium, cyanide (as free cyanide), chromium, fluoride, mercury, nickel, selenium, or thallium.

2. Nitrate and nitrite. Compliance with the PMCL is determined based on one sample from each sampling point if the levels of these contaminants are below the PMCLs. Where nitrate or nitrite sample results exceed the PMCL, the waterworks owner shall take a confirmation sample from the same sampling point that exceeded the PMCL within 24 hours of the waterworks' receipt of the analytical results of the first sample. The results of the initial and confirmation sample shall be averaged to determine compliance with this subdivision. Waterworks owners unable to comply with the 24-hour sampling requirement must immediately notify the consumers in the area served by the waterworks in accordance with 12 VAC 5-590-540. Waterworks exercising this option must take and analyze a confirmation sample within two weeks of notification of the analytical results of the first sample. The commissioner may require more frequent monitoring. The commissioner has the discretion to delete results of obvious sampling errors.

3. Compliance with the PMCL for arsenic is determined by the average of four analyses made pursuant to 12 VAC 5-590-370 B 1 d (6). When the average is rounded off to the same number of significant figures as the PMCL and exceeds the PMCL the owner shall notify the commissioner and give notice to the public pursuant to 12 VAC 5-590-540. Monitoring after public notification shall be at a frequency designated by the commissioner and shall continue until the PMCL has not been exceeded in two successive samples or until a monitoring schedule as a condition to a variance, exemption or enforcement action shall become effective.

C. Organic chemicals.

1. VOCs and SOCs. A confirmation sample shall be required for positive results for contaminants listed in Table 2.3. The commissioner has the discretion to delete results of obvious sampling errors from this calculation.

a. The results of the initial and confirmation sample shall be averaged to determine the waterworks' compliance in accordance with subdivision 1 b of this subsection.

b. Compliance with Table 2.3 shall be determined based on the analytical results obtained at each sampling point.

(1) For waterworks which are conducting monitoring more frequently than annually, compliance is determined by a running annual average of all samples taken at each sampling point. If the annual average of any sampling point is greater than the PMCL, then the waterworks is out of compliance. If the initial sample or a subsequent sample would cause the annual average to be exceeded, then the waterworks is out of compliance immediately. Any samples below the detection limit shall be calculated as zero for purposes of determining the annual average. (Note: Refer to detection definition at 12 VAC 5-590-370 B 2 h.)

(2) If monitoring is conducted annually, or less frequently, the waterworks is out of compliance if the level of a contaminant at any sampling point is greater than the PMCL. The determination of compliance will be based on the average of the initial and confirmation sample.

2. Disinfectant residuals, disinfection byproducts and disinfection byproduct precursors.

a. Trihalomethanes. Compliance with 12 VAC 5-590-370 B 3 a shall be determined based on a running annual average of quarterly samples taken in accordance with 12 VAC 5-590-370 B 3 a (1) through B 3 a (10) (e).

b. Compliance with 12 VAC 5-590-370 B 3 b through B 3 k is as follows:

(1) General requirements.

(a) Where compliance is based on a running annual average of monthly or quarterly samples or averages and the waterworks fails to monitor for TTHM, HAA5, or bromate, this failure to monitor will be treated as a monitoring violation for the entire period covered by the annual average. Where compliance is based on a running annual average of monthly or quarterly samples or averages and the waterworks’ failure to monitor makes it impossible to determine compliance with MRDLs for chlorine and chloramines, this failure to monitor will be treated as a monitoring violation for the entire period covered by the annual average.

(b) All samples taken and analyzed under the provisions of this subpart must be included in determining compliance, even if that number is greater than the minimum required.

(c) If during the first year of monitoring under 12 VAC 5-590-370 B 3 b, any individual quarter's average will cause the running annual average of that waterworks to exceed the PMCL in Table 2.13, the waterworks is out of compliance at the end of that quarter.

(2) Disinfection byproducts.

(a) TTHMs and HAA5.

(i) For waterworks monitoring quarterly, compliance with PMCLs in Table 2.13 must be based on a running annual arithmetic average, computed quarterly, of quarterly arithmetic averages of all samples collected by the waterworks as prescribed by 12 VAC 5-590-370 B 3 f (1).

(ii) For waterworks monitoring less frequently than quarterly, the waterworks demonstrate PMCL compliance if the average of samples taken that year under the provisions of 12 VAC 5-590-370 B 3 f (1) does not exceed the PMCLs in Table 2.13. If the average of these samples exceeds the PMCL, the waterworks must increase monitoring to once per quarter per treatment plant and such a waterworks is not in violation of the PMCL until it has completed one year of quarterly monitoring, unless the result of fewer then four quarter of monitoring will cause the running annual average to exceed the PMCL, in which case the waterworks is in violation at the end of that quarter. Waterworks required to increase monitoring frequency to quarterly monitoring must calculate compliance by including the sample that triggered the increase monitoring plus the following three quarter of monitoring.

(iii) If the running annual arithmetic average of quarterly averages covering any consecutive four-quarter period exceeds the PMCL in Table 2.13, the waterworks is in violation of the PMCL and must notify the public pursuant to 12 VAC 5-590-540 in addition to reporting to the commissioner pursuant to 12 VAC 5-590-530.

(iv) If a waterworks fails to complete four consecutive quarters of monitoring, compliance with the PMCL in Table 2.13 for the last four-quarter compliance period must be based on an average of the available data.

(b) Bromate. Compliance must be based on a running annual arithmetic average, computed quarterly, of monthly samples (or, for months in which the waterworks takes more than one sample, the average of all samples taken during the month) collected by the waterworks as prescribed by 12 VAC 5-590-370 B 3 h. If the average of samples covering any consecutive four-quarter period exceeds the PMCL in Table 2.13, the waterworks is in violation of the PMCL and must notify the public pursuant to 12 VAC 5-590-540, in addition to reporting to the commissioner pursuant to 12 VAC 5-590-530. If a waterworks fails to complete 12 consecutive months' monitoring, compliance with the PMCL for the last four-quarter compliance period must be based on an average of the available data.

(c) Chlorite. Compliance must be based on an arithmetic average of each three sample set taken in the distribution system as prescribed by 12 VAC 5-590-370 B 3 g (1) (b) and (c). If the arithmetic average of any three sample set exceeds the PMCL in Table 2.13, the waterworks is in violation of the PMCL and must notify the public pursuant to 12 VAC 5-590-540, in addition to reporting to the commissioner pursuant to 12 VAC 5-590-530.

(3) Disinfectant residuals.

(a) Chlorine and chloramines.

(i) Compliance must be based on a running annual arithmetic average, computed quarterly, of monthly averages of all samples collected by the waterworks under 12 VAC 5-590-370 B 3 i (1) (a). If the average covering any consecutive four-quarter period exceeds the MRDL in Table 2.12, the waterworks is in violation of the MRDL and must notify the public pursuant to 12 VAC 5-590-540, in addition to reporting to the commissioner pursuant to 12 VAC 5-590-530.

(ii) In cases where waterworks switch between the use of chlorine and chloramines for residual disinfection during the year, compliance must be determined by including together all monitoring results of both chlorine and chloramines in calculating compliance. Reports submitted pursuant to 12 VAC 5-590-530 must clearly indicate which residual disinfectant was analyzed for each sample.

(b) Chlorine dioxide.

(i) Acute violations. Compliance must be based on consecutive daily samples collected by the waterworks under 12 VAC 5-590-370 B 3 i (2) (a). If any daily sample taken at the entrance to the distribution system exceeds the MRDL in Table 2.12, and on the following day one (or more) of the three samples taken in the distribution system exceed the MRDL, the waterworks is in violation of the MRDL and must take immediate corrective action to lower the level of chlorine dioxide below the MRDL and must notify the public pursuant to the procedures for acute health risks in 12 VAC 5-590-540 B 3 d in addition to reporting to the commissioner in pursuant to 12 VAC 5-590-530. Failure to take samples in the distribution system the day following an exceedance of the chlorine dioxide MRDL at the entrance to the distribution system will also be considered an MRDL violation and the waterworks must notify the public of the violation in accordance with the provisions for acute violations under 12 VAC 5-590-540 B 3 e in addition to reporting to the commissioner in pursuant to 12 VAC 5-590-530.

(ii) Nonacute violations. Compliance must be based on consecutive daily samples collected by the waterworks under 12 VAC 5-590-370 B 3 i (2) (a). If any two consecutive daily samples taken at the entrance to the distribution system exceed the MRDL in Table 2.12 and all distribution system samples taken are below the MRDL, the waterworks is in violation of the MRDL and must take corrective action to lower the level of chlorine dioxide below the MRDL at the point of sampling and shall notify the public pursuant to the procedures for nonacute health risks in Appendix F Paragraph 78 in addition to reporting to the commissioner in pursuant to 12 VAC 5-590-530. Failure to monitor at the entrance to the distribution system the day following an exceedance of the chlorine dioxide MRDL at the entrance to the distribution system is also an MRDL violation and the waterworks must notify the public of the violation in accordance with the provisions for nonacute violations under Appendix F Paragraph 78 in addition to reporting to the commissioner in pursuant to 12 VAC 5-590-530.

(c) Disinfection byproduct precursors (DBPP). Compliance must be determined as specified by 12 VAC 5-590-420 H 3. Waterworks may begin monitoring to determine whether Step 1 TOC removals can be met 12 months prior to the compliance date for the waterworks. This monitoring is not required and failure to monitor during this period is not a violation. However, any waterworks that does not monitor during this period, and then determines in the first 12 months after the compliance date that it is not able to meet the Step 1 requirements in 12 VAC 5-590-420 H 2 b and must therefore apply for alternate minimum TOC removal (Step 2) requirements, is not eligible for retroactive approval of alternate minimum TOC removal (Step 2) requirements as allowed pursuant to 12 VAC 5-590-420 H 2 c and is in violation. Waterworks may apply for alternate minimum TOC removal (Step 2) requirements any time after the compliance date. For waterworks required to meet Step 1 TOC removals, if the value calculated under 12 VAC 5-590-420 H 3 a (5) is less than 1.00, the waterworks is in violation of the treatment technique requirements and must notify the public pursuant to 12 VAC 5-590-540 in addition to reporting to the commissioner pursuant to 12 VAC 5-90-530.

D. Radiological results (gross alpha, total radium and man-made radioactivity). Compliance with the radiological Primary Maximum Contaminant Levels shall be based on the annual average results. Primary Maximum Contaminant Levels are indicated in Table 2.5. Sampling for radiological analysis shall be in compliance with 12 VAC 5-590-400 A 1 and A 2. Furthermore, compliance shall be determined by rounding off results to the same number of significant figures as the Primary Maximum Contaminant Level for the substance in question.

E. Lead and copper action levels.

1. The lead action level is exceeded if the concentration of lead in more than 10% of tap water samples collected during any monitoring period conducted in accordance with 12 VAC 5-590-370 B 6 a is greater than 0.015 mg/L (i.e., if the "90th percentile" lead level is greater than 0.015 mg/L).

2. The copper action level is exceeded if the concentration of copper in more than 10% of tap water samples collected during any monitoring period conducted in accordance with 12 VAC 5-590-370 B 6 a is greater than 1.3 mg/L (i.e., if the "90th percentile" copper level is greater than 1.3 mg/L).

3. The 90th percentile lead and copper levels shall be computed as follows:

a. The results of all lead or copper samples taken during a monitoring period shall be placed in ascending order from the sample with the lowest concentration to the sample with the highest concentration. Each sampling result shall be assigned a number, ascending by single integers beginning with the number 1 for the sample with the lowest contaminant level. The number assigned to the sample with the highest contaminant level shall be equal to the total number of samples taken.

b. The number of samples taken during the monitoring period shall be multiplied by 0.9.

c. The contaminant concentration in the numbered sample yielded by the calculation in subdivision 3 b of this subsection is the 90th percentile contaminant level.

d. For waterworks serving fewer than 100 people that collect five samples per monitoring period, the 90th percentile is computed by taking the average of the highest and second highest concentrations.

F. Turbidity. The requirements in this subsection apply to filtered waterworks until June 29, 1993. The requirements in this section apply to unfiltered waterworks with surface water sources or groundwater sources under the direct influence of surface water that are required to install filtration equipment until June 29, 1993, or until filtration is installed, whichever is later. When a sample exceeds the PMCL for turbidity a confirmation sample shall be collected for analysis as soon as possible. In cases where a turbidimeter is required at the waterworks, the preferable resampling time is within one hour of the initial sampling. The repeat sample shall be the sample used for the purpose of calculating the monthly average. Compliance for public notification purposes shall be based on the monthly averages of the daily samples. However, public notification is also required if the average of samples taken on two consecutive days exceeds five NTU.

G. All analyses for PMCL and action level compliance determinations shall be consistent with current Environmental Protection Agency Regulations found at 40 CFR 141.

12 VAC 5-590-420. Treatment technique requirements.

This section establishes treatment technique requirements in lieu of maximum contaminant levels for specified contaminants. Failure to meet any requirement of this section after the applicable date specified is a treatment technique violation.

A. Beginning June 29, 1993, the filtration and disinfection provisions of this section are required treatment techniques for any waterworks supplied by a surface water source and waterworks supplied by a groundwater source under the direct influence of surface water. Prior to that date, waterworks are governed by the disinfection requirements of 12 VAC 5-590-500. In addition, this section establishes treatment technique requirements in lieu of PMCL's for the following contaminants: Giardia lamblia, viruses, heterotrophic bacteria (HPC), Legionella Cryptosporidium (for waterworks serving at least 10,000 people and using surface water or groundwater under the direct influence of surface water), and turbidity. Each waterworks with a surface water source or a groundwater source under the direct influence of surface water shall provide treatment of that source water that complies with these treatment technique requirements. The treatment technique requirements consist of installing and properly operating water treatment processes which reliably achieve:

1. At least 99.9% (3-log) removal and/or inactivation of Giardia lamblia cysts between a point where the raw water is not subject to recontamination by surface water runoff and a point downstream before or at the first customer; and

2. At least 99.99% (4-log) removal and/or inactivation of viruses between a point where the raw water is not subject to recontamination by surface water runoff and a point downstream before or at the first customer.

3. Beginning January 1, 2002, waterworks serving at least 10,000 people shall also reliably achieve at least 99% (2-log) removal of Cryptosporidium between a point where the raw water is not subject to recontamination by surface water runoff and a point downstream before or at the first customer.

B. A waterworks using a surface water source or a groundwater source under the direct influence of surface water is considered to be in compliance with the requirements of subsection A of this section if it meets the following disinfection and filtration requirements:

1. Disinfection. Waterworks with a surface water source or a groundwater source under the direct influence of surface water must provide disinfection treatment in accordance with this section by June 29, 1993.

a. The disinfection treatment must be sufficient to ensure that the total treatment processes of that waterworks achieve at least 99.9% (3-log) inactivation and/or removal of Giardia lamblia cysts and at least 99.99% (4-log) inactivation and/or removal of viruses.

b. The residual disinfectant concentration in the water entering the distribution system cannot be less than 0.2 mg/L for more than four hours.

c. The residual disinfectant concentration in the distribution system, measured as total chlorine, combined chlorine, or chlorine dioxide cannot be undetectable in more than 5.0% of the samples each month, for any two consecutive months that the waterworks serves water to the public. Water in the distribution system with a heterotrophic bacteria concentration less than or equal to 500/mL, measured as heterotrophic plate count (HPC) is deemed to have a detectable disinfectant residual for purposes of determining compliance with this requirement. Thus, the value "V" in percent in the following formula cannot exceed 5.0% in one month, for any two consecutive months.

V = [(c + d + e) / (a + b)] X 100

a = number of instances where the residual disinfectant concentration is measured;

b = number of instances where the residual disinfectant concentration is not measured but HPC is measured;

c = number of instances where the residual disinfectant concentration is measured but not detected and no HPC is measured;

d = number of instances where no residual disinfectant concentration is detected and where the HPC is greater than500/mL; and

e = number of instances where the residual disinfectant concentration s not measured and HPC is greater than500/mL.

d. The division may determine, based on site-specific considerations, that a waterworks owner has no means for having a sample transported and analyzed for HPC by a certified laboratory under the requisite time and temperature conditions and the waterworks is providing adequate disinfection in the distribution system, that the requirements of subdivision B 1 c of this section does not apply.

2. Filtration. (Also see 12 VAC 5-590-880.) All waterworks that use a surface water source or a groundwater source under the direct influence of surface water shall provide filtration treatment by June 29, 1993, by using one of the following methods:

a. Conventional filtration or direct filtration.

(1) The turbidity level of representative samples of a waterworks' filtered water shall be less than or equal to 0.5 NTU in at least 95% of the measurements taken each month, except that if the division determines that the system is capable of achieving at least 99.9% removal (3-log) and/or inactivation of Giardia lamblia cysts at some turbidity level higher than 0.5 NTU in at least 95% of the measurements taken each month, the division may substitute this higher turbidity limit for that waterworks. However, in no case may the division approve a turbidity limit that allows more than one NTU in more than 5.0% of the samples taken each month.

(2) The turbidity level of representative samples of a waterworks' filtered water shall at no time exceed five NTU.

(3) Beginning January 1, 2002, waterworks serving at least 10,000 people that use conventional filtration treatment or direct filtration must:

(a) Achieve a filtered water turbidity of less than or equal to 0.3 NTU in at least 95% of the measurements taken each month. Samples must be representative of the waterworks' filtered water.

(b) The turbidity level of representative samples of a system's filtered water must at no time exceed 1 NTU, measured as specified in 12 VAC 5-590-440.

(c) A system that uses lime softening may acidify representative samples prior to analysis using a protocol approved by the commissioner.

b. Slow sand filtration.

(1) The turbidity level of representative samples of a waterworks' filtered water must be less than or equal to one NTU in at least 95% of the measurements taken each month, except that if the division determines there is no significant interference with disinfection at a higher turbidity level, the division may substitute this higher turbidity limit for that waterworks.

(2) The turbidity level of representative samples of a waterworks' filtered water shall at no time exceed five NTU.

c. Diatomaceous earth filtration.

(1) The turbidity level of representative samples of a waterworks' filtered water shall be less than or equal to one NTU in at least 95% of the measurements taken each month.

(2) The turbidity level of representative samples of a waterworks' filtered water shall at no time exceed five NTU.

d. Other filtration technologies. A waterworks owner may use a filtration technology not listed in subdivisions 2 a through c of this subsection if the owner demonstrates to the division (by pilot plant studies or other means) that the alternative filtration technology, in combination with disinfection treatment, achieves 99.9% removal (3-log) and/or inactivation of Giardia lamblia cysts and 99.99% removal (4-log) and/or inactivation of viruses, and beginning January 1, 2002, for waterworks serving at least 10,000 people, 99% of Cryptosporidium oocysts. For a waterworks owner that makes this demonstration, the requirements of subdivision B 2 b of this section also apply a turbidity limit will be established by the commissioner, which the waterworks must meet at least 95% of the time. In addition, the commissioner will establish a maximum turbidity limit that the waterworks must not exceed at any time. These turbidity limits shall consistently achieve the removal rates and/or inactivation rates stated in this subdivision.

e. Each waterworks using a surface water source or groundwater source under the direct influence of surface water shall be operated by licensed operators of the appropriate classification as per the Virginia Board for Waterworks and Wastewater Works Operators Regulations (18 VAC 155-20-10 et seq.).

f. If the division has determined that a waterworks has a surface water source or a groundwater source under the direct influence of surface water, filtration is required. The waterworks shall provide disinfection during the interim before filtration is installed as follows:

(1) The residual disinfectant concentration in the distribution system cannot be less than 2.0 mg/L for more than four hours.

(2) The waterworks owner shall issue continuing boil water notices through the public notification procedure in 12 VAC 5-590-540 until such time as the required filtration equipment is installed.

(3) As an alternative to subdivisions B f 2 (1) and (2) of this section, the waterworks owner may demonstrate that the source can meet the appropriate C-T values shown in Appendix L and be considered to satisfy the requirements for 99.9% removal of Giardia cysts and virus, respectively. In addition, the waterworks owner must comply with the following:

(a) Justify that other alternative sources of supply meeting these regulations are not immediately available.

(b) Analysis of the source is performed quarterly for the contaminants listed in Tables 2.2, 2.3, and 2.4. The primary maximum contaminant levels shall not be exceeded.

(c) Daily turbidity monitoring and maintenance of the turbidity level not to exceed five NTU.

(d) MPN analysis of the raw water based on the minimum sample frequency chart below:

| Population Served | Coliform Samples/Week |
| --- | --- |
| less than or equal to 500 | 1 |
| 501 - 3,300 | 2 |
| 3,301 - 10,000 | 3 |
| 10,001 - 25,000 | 4 |
| >25,000 | 5 |

Note: Must be taken on separate days.

(e) Bacteriological sampling of the distribution system at a frequency of twice that required by Table 2.1.

C. Lead and copper corrosion control techniques.

1. Corrosion control treatment requirements. The owners of all community and nontransient noncommunity waterworks shall install and operate optimum corrosion control treatment by completing the corrosion control treatment requirements described below which are applicable to such waterworks owners under subdivision C 2 of this section.

a. Waterworks owners proposal regarding corrosion control treatment. Based upon the results of lead and copper tap monitoring and water quality parameter monitoring, the owners of small and medium-size waterworks exceeding the lead or copper action level shall propose installation of one or more of the corrosion control treatments listed in subdivision C 1 c (1) of this section which the waterworks owner believes constitutes optimal corrosion control for that waterworks. The commissioner may require the waterworks owner to conduct additional water quality parameter monitoring in accordance with 12 VAC 5-590-370 B 6 b (2) of this section to assist the commissioner in reviewing the proposal.

b. Applicability of studies of corrosion control treatment (applicable to small and medium-size waterworks). The commissioner may require the owner of any small or medium-size waterworks that exceeds the lead or copper action level to perform corrosion control studies under subdivision C 1 c of this section to identify optimal corrosion control treatment for the waterworks.

c. Corrosion control studies.

(1) The owner of any waterworks required by the commissioner to perform corrosion control studies shall evaluate the effectiveness of each of the following treatments, and, if appropriate, combinations of the following treatments to identify the optimal corrosion control treatment for that waterworks:

(a) Alkalinity and pH adjustment;

(b) Calcium hardness adjustment; and

(c) The addition of a phosphate or silicate based corrosion inhibitor at a concentration sufficient to maintain an effective corrosion inhibitor residual concentration in all test tap samples.

(2) The waterworks owner shall evaluate each of the corrosion control treatments using either pipe rig/loop tests, metal coupon tests, partial-system tests, or analyses based on documented analogous treatments with other waterworks of similar size, water chemistry and distribution system configuration.

(3) The waterworks owner shall measure the following water quality parameters in any tests conducted under this paragraph before and after evaluating the corrosion control treatments listed above:

(a) Lead;

(b) Copper;

(c) pH;

(d) Alkalinity;

(e) Calcium;

(f) Conductivity;

(g) Orthophosphate (when an inhibitor containing a phosphate compound is used);

(h) Silicate (when an inhibitor containing a silicate compound is used);

(i) Water temperature.

(4) The waterworks owner shall identify all chemical or physical constraints that limit or prohibit the use of a particular corrosion control treatment and document such constraints with at least one of the following:

(a) Data and documentation showing that a particular corrosion control treatment has adversely affected other water treatment processes when used by another waterworks with comparable water quality characteristics; and/or

(b) Data and documentation demonstrating that the waterworks has previously attempted to evaluate a particular corrosion control treatment and has found that the treatment is ineffective or adversely affects other water quality treatment processes.

(5) The waterworks owner shall evaluate the effect of the chemicals used for corrosion control treatment on other water quality treatment processes.

(6) On the basis of an analysis of the data generated during each evaluation, the waterworks owner shall propose to the field office in writing, the treatment option that the corrosion control studies indicate constitutes optimal corrosion control treatment for that waterworks. The owner shall provide a rationale for its recommendation along with all supporting documentation specified in subdivision C 1 c (1) through (5) of this section.

d. Approval of optimal corrosion control treatment.

(1) Based upon consideration of available information including, where applicable, studies performed under subdivision C 1 c of this section and a waterworks' owner's proposed treatment alternative, the commissioner shall either approve the corrosion control treatment option recommended by the owner, or designate alternative corrosion control treatment(s) from among those listed in subdivision C 1 c (1) of this section. When approving optimal treatment the commissioner shall consider the effects that additional corrosion control treatment will have on water quality parameters and on other water quality treatment processes.

(2) The commissioner shall notify the waterworks owner of its determination on optimal corrosion control treatment in writing and explain the basis for this determination. If the commissioner requests additional information to aid a review, the owner shall provide the information.

e. Installation of optimal corrosion control. Each waterworks owner shall properly install and operate throughout the waterworks the optimal corrosion control treatment approved by the commissioner under subdivision C 1 d of this section and under 12 VAC 5-590-190.

f. Commissioner's review of treatment and specification of optimal water quality control parameters.

(1) The commissioner shall evaluate the results of all lead and copper tap samples and water quality parameter samples submitted by the waterworks owner and determine whether the owner has properly installed and operated the optimal corrosion control treatment approved by the commissioner in subdivision C 1 d of this section. Upon reviewing the results of tap water and water quality parameter monitoring by the owner, both before and after the waterworks installs optimal corrosion control treatment, the commissioner shall designate:

(a) A minimum value or a range of values for pH measured at each entry point to the distribution system;

(b) A minimum pH value, measured in all tap samples. Such value shall be equal to or greater than 7.0, unless the commissioner determines that meeting a pH level of 7.0 is not technologically feasible or is not necessary for the waterworks owner to optimize corrosion control;

(c) If a corrosion inhibitor is used, a minimum concentration or a range of concentrations for the inhibitor, measured at each entry point to the distribution system and in all tap samples, that the commissioner determines is necessary to form a passivating film on the interior walls of the pipes of the distribution system;

(d) If alkalinity is adjusted as part of optimal corrosion control treatment, a minimum concentration or a range of concentrations for alkalinity, measured at each entry point to the distribution system and in all tap samples;

(e) if calcium carbonate stabilization is used as part of corrosion control, a minimum concentration or a range of concentrations for calcium, measured in all tap samples.

(2) The values for the applicable water quality control parameters listed above shall be those that the commissioner determines to reflect optimal corrosion control treatment for the waterworks. The commissioner may designate values for additional water quality control parameters determined by the commissioner to reflect optimal corrosion control for the waterworks. The commissioner shall notify the waterworks owner in writing of these determinations and explain the basis for its decisions.

g. Continued operation and monitoring. The owners of all waterworks shall maintain water quality parameter values at or above minimum values or within ranges designated by the commissioner under subdivision C 1 f of this section in each sample collected under 12 VAC 5-590-370 B 6 b (4). If the water quality parameter value of any sample is below the minimum value or outside the range designated by the commissioner, then the waterworks is out of compliance with this paragraph. As specified in 12 VAC 5-590-370 B 6 b (4), the waterworks owner may take a confirmation sample for any water quality parameter value no later than three days after the first sample. If a confirmation sample is taken, the result must be averaged with the first sampling result and the average must be used for any compliance determinations under this paragraph. The commissioner has the discretion to delete results of obvious sampling errors from this calculation.

h. Modification of the commissioner's treatment decisions. Upon his own initiative or in response to a request by a waterworks owner or other interested party, the commissioner may modify its determination of the optimal corrosion control treatment under 12 VAC 5-590-420 subdivision C 1 d of this section or optimal water quality control parameters under 12 VAC 5-590-420 subdivision C 1 f of this section. A request for modification by an owner or other interested party shall be in writing, explain why the modification is appropriate, and provide supporting documentation. The commissioner may modify the determination where it is concluded that such change is necessary to ensure that the waterworks continues to optimize corrosion control treatment. A revised determination shall be made in writing, set forth the new treatment requirements, explain the basis for the commissioner's decision, and provide an implementation schedule for completing the treatment modifications.

2. Corrosion control treatment steps.

a. Waterworks owners shall complete the applicable corrosion control treatment requirements described in 12 VAC 5-590-420 subdivision C 1 of this section by the deadlines established in this section.

(1) The owner of a large waterworks (serving greater than 50,000 persons) shall complete the corrosion control treatment steps specified in 12 VAC 5-590-420 subdivision C 2 d of this section, unless the owner is deemed to have optimized corrosion control under 12 VAC 5-590-420 subdivision C 2 b (2) of this section or 12 VAC 5-590-420 C 2 b (3) of this section.

(2) The owner of a small waterworks (serving less than 3,300 persons) and a medium-size waterworks (serving greater than 3,300 and less than 50,000 persons) shall complete the corrosion control treatment steps specified in 12 VAC 5-590-420 subdivision C 2 e of this section, unless the owner is deemed to have optimized corrosion control under 12 VAC 5-590-420 subdivision C 2 b (1) through (3) of this section.

b. A waterworks owner is deemed to have optimized corrosion control and is not required to complete the applicable corrosion control treatment steps identified in this section if the waterworks satisfies one of the following criteria:

(1) The owner of a small or medium-size waterworks is deemed to have optimized corrosion control if the waterworks meets the lead and copper action levels during each of two consecutive six-month monitoring periods conducted in accordance with 12 VAC 5-590-370 B 6 a.

(2) Any waterworks owner may be deemed by the commissioner to have optimized corrosion control treatment if the owner demonstrates to the satisfaction of the commissioner that the owner has conducted activities equivalent to the corrosion control steps applicable to such waterworks under this section. If the commissioner makes this determination, the owner shall be provided with a written notice explaining the basis for the decision and the notice shall specify the water quality control parameters representing optimal corrosion control in accordance with 12 VAC 5-590-420 subdivision C 1 f of this section. A waterworks owner shall provide the commissioner with the following information in order to support a determination under this paragraph:

(a) The results of all test samples collected for each of the water quality parameters in 12 VAC 5-590-420 subdivision C 1 c (3) of this section.

(b) A report explaining the test methods used by the waterworks owner to evaluate the corrosion control treatments listed in 12 VAC 5-590-420 subdivision C 1 c (1) of this section, the results of all tests conducted, and the basis for the owner's selection of optimal corrosion control treatment;

(c) A report explaining how corrosion control has been installed and how it is being maintained to insure minimal lead and copper concentrations at consumers' taps; and

(d) The results of tap water samples collected in accordance with 12 VAC 5-590-370 B 6 a at least once every six months for one year after corrosion control has been installed.

(3) Any waterworks is deemed to have optimized corrosion control if the owner submits results of tap water monitoring conducted in accordance with 12 VAC 5-590-370 B 6 a and source water monitoring conducted in accordance with 12 VAC 5-590-370 B 6 c that demonstrates for two consecutive six-month monitoring periods that the difference between the 90th percentile tap water lead level computed under 12 VAC 5-590-410 E, and the highest source water lead concentration, is less than the P Q L for lead (0.005 mg/L).

c. The owner of any small or medium-size waterworks that is required to complete the corrosion control steps due to the exceedance of the lead or copper action level may cease completing the treatment steps whenever the waterworks meets both action levels during each of two consecutive monitoring periods conducted pursuant to 12 VAC 5-590-370 B 6 a and submits the results to the field office. If any such waterworks thereafter exceeds the lead or copper action level during any monitoring period, the owner shall recommence completion of the applicable treatment steps, beginning with the first treatment step which was not previously completed in its entirety. The commissioner may require the owner to repeat treatment steps previously completed where the commissioner determines that this is necessary to properly implement the treatment requirements of this section. The commissioner shall notify the owner in writing of such a determination and explain the basis for its decision. The requirement for the owner of any small- or medium-sized waterworks to implement corrosion control treatment steps in accordance with subdivision 2 e of this subsection (including waterworks deemed to have optimized corrosion control under subdivision 2 b (1) of this subsection) is triggered whenever any small- or medium-sized waterworks exceeds the lead or copper action level.

d. Treatment steps and deadlines for large waterworks. Except as provided in 12 VAC 5-590-420 subdivisions C 2 b (2) and 12 VAC 5-590-420 C 2 b (3) of this section, owners of large waterworks shall complete the following corrosion control treatment steps (described in the referenced portions of 12 VAC 5-590-420 subdivision C 1 of this section, 12 VAC 5-590-370 B 6 a and b) by the indicated dates.

(1) Step 1: The waterworks owner shall conduct initial monitoring (12 VAC 5-590-370 B 6 a (4) (a) and 12 VAC 5-590-370 B 6 b (2)) during two consecutive six-month monitoring periods by January 1, 1993.

(2) Step 2: The waterworks owner shall complete corrosion control studies (12 VAC 5-590-420 C 1 c) and submit the study and recommendations to the commissioner (12 VAC 5-590-200) by July 1, 1994.

(3) Step 3: The commissioner shall approve optimal corrosion control treatment (12 VAC 5-590-420 C 1 d) by January 1, 1995.

(4) Step 4: The waterworks owner shall install optimal corrosion control treatment (12 VAC 5-590-420 C 1 e) by January 1, 1997.

(5) Step 5: The waterworks owner shall complete follow-up sampling (12 VAC 5-590-370 B 6 a (4) (b) and 12 VAC 5-590-370 B 6 b (3)) by January 1, 1998.

(6) Step 6: The commissioner shall review installation of treatment and designate optimal water quality control parameters (12 VAC 5-590-420 C 1 f) by July 1, 1998.

(7) Step 7: The waterworks owner shall operate the waterworks in compliance with the commissioner-specified optimal water quality control parameters (12 VAC 5-590-420 C 1 g) and continue to conduct tap sampling (12 VAC 5-590-370 B 6 a (4) (c) and 12 VAC 5-590-370 B 6 b (4)).

e. Treatment steps and deadlines for small and medium-size waterworks. Except as provided in 12 VAC 5-590-420 C 2 b, owners of small- and medium-size waterworks shall complete the following corrosion control treatment steps (described in the referenced portions of 12 VAC 5-590-420 C 1, 12 VAC 5-590-370 B 6 a and 12 VAC 5-590-370 B 6 b) by the indicated time periods.

(1) Step 1: The waterworks owner shall conduct initial tap sampling (12 VAC 5-590-370 B 6 a (4) (a) and 12 VAC 5-590-370 B 6 b (2)) until the waterworks either exceeds the lead or copper action level or becomes eligible for reduced monitoring under 12 VAC 5-590-370 B 6 a (4) (d). The owner of a waterworks exceeding the lead or copper action level shall propose optimal corrosion control treatment (12 VAC 5-590-420 C 1 a) within six months after it exceeds one of the action levels.

(2) Step 2: Within 12 months after a waterworks exceeds the lead or copper action level, the commissioner may require the waterworks owner to perform corrosion control studies (12 VAC 5-590-420 C 1 b). If the commissioner does not require the owner to perform such studies, the commissioner shall specify optimal corrosion control treatment (12 VAC 5-590-420 C 1 d) within the following timeframes:

(a) For medium-size waterworks, within 18 months after such waterworks exceeds the lead or copper action level,

(b) For small waterworks, within 24 months after such waterworks exceeds the lead or copper action level.

(3) Step 3: If the commissioner requires a waterworks owner to perform corrosion control studies under Step 2, the waterworks owner shall complete the studies (12 VAC 5-590-420 C 1 c) and submit the study and recommendations to the commissioner (12 VAC 5-590-200) within 18 months after the commissioner requires that such studies be conducted.

(4) Step 4: If the waterworks has performed corrosion control studies under Step 2, the commissioner shall designate optimal corrosion control treatment (12 VAC 5-590-420 C 1 d) within six months after completion of Step 3.

(5) Step 5: The waterworks shall install optimal corrosion control treatment (12 VAC 5-590-420 C 1 e) within 24 months after the commissioner designates such treatment.

(6) Step 6: The waterworks owner shall complete follow-up sampling (12 VAC 5-590-370 B 6 a (4) (b) and 12 VAC 5-590-370 B 6 b (3)) within 36 months after the commissioner designates optimal corrosion control treatment.

(7) Step 7: The commissioner shall review the waterworks owner's installation of treatment and designate optimal water quality control parameters (12 VAC 5-590-420 C 1 f) within six months after completion of Step 6.

(8) Step 8: The waterworks owner shall operate in compliance with the commissioner designated optimal water quality control parameters (12 VAC 5-590-420 C 1 g) and continue to conduct tap sampling (12 VAC 5-590-370 B 6 a (4) (c) and 12 VAC 5-590-370 B 6 b(4)).

D. Water supply (source water) treatment requirements for lead and copper. The owner of any waterworks exceeding the lead or copper action level shall complete the applicable water supply monitoring and treatment requirements (described in the referenced portions of 12 VAC 5-590-420 subdivision D 2 of this section, and in 12 VAC 5-590-370 B 6 a, and 12 VAC 5-590-370 B 6 c) by the following deadlines.

1. Deadlines for completing water supply treatment steps.

a. Step 1: The owner of a waterworks exceeding the lead or copper action level shall complete lead and copper water supply monitoring (12 VAC 5-590-370 B 6 c (2)) and make a treatment proposal to the appropriate field office within six months after exceeding the lead or copper action level.

b. Step 2: The commissioner shall make a determination regarding the need for water supply treatment (12 VAC 5-590-420 D 2 b) within six months after submission of monitoring results under step 1.

c. Step 3: If the commissioner requires installation of water supply treatment, the waterworks owner shall install the treatment (12 VAC 5-590-420 D 3) within 24 months after completion of step 2.

d. Step 4: The waterworks owner shall complete follow-up tap water monitoring (12 VAC 5-590-370 B 6 a (4) (b)) and water supply lead and copper monitoring (12 VAC 5-590-370 B 6 c (3)) within 36 months after completion of step 2.

e. Step 5: The commissioner shall review the waterworks owner's installation and operation of water supply treatment and specify maximum permissible water supply lead and copper levels (12 VAC 5-590-420 D 4) within six months after completion of step 4.

f. Step 6: The waterworks owner shall operate in compliance with the commissioner-specified maximum permissible lead and copper water supply levels (12 VAC 5-590-420 D 4) and continue water supply monitoring (12 VAC 5-590-370 B 6 c (4) (a)).

2. Description of water supply treatment requirements.

a. Waterworks treatment recommendation. The owner of any waterworks which exceeds the lead or copper action level shall propose in writing to the appropriate field office, the installation and operation of one of the water supply treatments listed in 12 VAC 5-590-420 subdivision D 2 b of this section. An owner may propose that no treatment be installed based upon a demonstration that water supply treatment is not necessary to minimize lead and copper levels at users' taps.

b. Commissioner's determination regarding water supply treatment. The commissioner shall complete an evaluation of the results of all water supply samples submitted by the waterworks owner to determine whether water supply treatment is necessary to minimize lead or copper levels in water delivered to users' taps. If the division determines that treatment is needed, the commissioner shall either require installation and operation of the water supply treatment recommended by the waterworks (if any) or require the installation and operation of another water supply treatment from among the following: ion exchange, reverse osmosis, lime softening or coagulation/filtration. If the commissioner requests additional information to aid in the review, the waterworks shall provide the information by the date specified by the commissioner in the request. The commissioner shall notify the waterworks in writing of the determination and set forth the basis for the decision.

3. Installation of water supply treatment. Each waterworks owner shall properly install and operate the water supply treatment designated by the commissioner under 12 VAC 5-590-420 subdivision D 2 b of this section.

4. Commissioner's review of water supply treatment and specification of maximum permissible water supply lead and copper levels. The commissioner shall review the water supply samples taken by the waterworks owner both before and after the waterworks owner installs water supply treatment, and determine whether the owner has properly installed and operated the water supply treatment designated by the commissioner. Based upon the review, the commissioner shall designate the maximum permissible lead and copper concentrations for finished water entering the distribution system. Such levels shall reflect the contaminant removal capability of the treatment properly operated and maintained. The commissioner shall notify the owner in writing and explain the basis for the decision.

5. Continued operation and maintenance. Each waterworks shall be operated to maintain lead and copper levels below the maximum permissible concentrations designated by the commissioner at each sampling point monitored in accordance with 12 VAC 5-590-370 B 6 c. The waterworks is out of compliance with this subdivision if the level of lead or copper at any sampling point is greater than the maximum permissible concentration designated by the commissioner.

6. Modification of the commissioner's treatment decisions. Upon his own initiative or in response to a request by a waterworks owner or other interested party, the commissioner may modify its determination of the water supply treatment under 12 VAC 5-590-420 D 2 b of this section, or may modify the maximum permissible lead and copper concentrations for finished water entering the distribution system under 12 VAC 5-590-420 subdivision D 4 of this section. A request for modification by an owner or other interested party shall be in writing, explain why the modification is appropriate, and provide supporting documentation. The commissioner may modify the determination where he concludes that such change is necessary to ensure that the waterworks continues to minimize lead and copper concentrations in water supplies. A revised determination shall be made in writing, set forth the new treatment requirements, explain the basis for the commissioner's decision, and provide an implementation schedule for completing the treatment modifications.

E. Lead service line replacement requirements.

1. Owners of waterworks that fail to meet the lead action level in tap samples taken pursuant to 12 VAC 5-590-370 B 6 a (4) (b), after installing corrosion control and/or water supply treatment (whichever sampling occurs later), shall replace lead service lines in accordance with the requirements of this section. If a waterworks is in violation of 12 VAC 5-590-420 subdivision C 2 of this section or 12 VAC 5-590-420 subsection D of this section for failure to install water supply or corrosion control treatment, the commissioner may require the owner to commence lead service line replacement under this section after the date by which the owner was required to conduct monitoring under 12 VAC 5-590-370 B 6 a (4) (b) has passed.

2. A waterworks owner shall replace annually at least 7.0% of the initial number of lead service lines in its distribution system. The initial number of lead service lines is the number of lead lines in place at the time the replacement program begins. The waterworks owner shall identify the initial number of lead service lines in its distribution system based upon a materials evaluation, including the evaluation required under 12 VAC 5-590-370 B 6 a (1) (a). The first year of lead service line replacement shall begin on the date the action level was exceeded in tap sampling referenced in 12 VAC 5-590-420 subdivision E 1 of this section.

3. A waterworks owner is not required to replace an individual lead service line if the lead concentration in all service line samples from that line, taken pursuant to 12 VAC 5-590-370 B 6 a (2) (c), is less than or equal to 0.015 mg/L.

4. A waterworks owner shall replace the entire service line (up to the building inlet) unless the owner demonstrates to the satisfaction of the commissioner under 12 VAC 5-590-420 subdivision E 5 of this section that it controls less than the entire service line. In such cases, the owner shall replace the portion of the line which the commissioner determines is under the owner's control. The owner shall notify the user served by the line that the waterworks owner will replace the portion of the service line under the waterworks owner's control and shall offer to replace the building owner's portion of the line, but is not required to bear the cost of replacing the building owner's portion of the line. For buildings where only a portion of the lead service line is replaced, the waterworks owner shall inform the resident(s) that the waterworks owner will collect a first flush tap water sample after partial replacement of the service line is completed if the resident(s) so desire. In cases where the resident(s) accept the offer, the waterworks owner shall collect the sample and report the results to the resident(s) within 14 days following partial lead service line replacement.

5. A waterworks owner is presumed to control the entire lead service line (up to the building inlet) unless the owner demonstrates to the satisfaction of the commissioner, in a letter submitted under 12 VAC 5-590-530 D 5 d, that the owner does not have any of the following forms of control over the entire line (as defined by state statutes, municipal ordinances, public service contracts or other applicable legal authority): authority to set standards for construction, repair, or maintenance of the line, authority to replace, repair, or maintain the service line, or ownership of the service line. The commissioner shall review the information supplied by the owner and determine whether the owner controls less than the entire service line and, in such cases, shall determine the extent of the waterworks owner's control. The commissioner's determination shall be in writing and explain the basis for the decision.

6. The commissioner shall require a waterworks owner to replace lead service lines on a shorter schedule than that required by this section, taking into account the number of lead service lines in the waterworks, where such a shorter replacement schedule is feasible. The commissioner shall make this determination in writing and notify the owner of the findings within 6 months after the waterworks is triggered into lead service line replacement based on monitoring referenced in 12 VAC 5-590-420 subdivision E 1 of this section.

7. Any waterworks owner may cease replacing lead service lines whenever first draw tap samples collected pursuant to 12 VAC 5-590-370 B 6 a (2) (b) meet the lead action level during each of two consecutive monitoring periods and the owner submits the results to the appropriate field office. If the first draw tap samples collected in any such waterworks thereafter exceeds the lead action level, the owner shall recommence replacing lead service lines, pursuant to 12 VAC 5-590-420 subdivision E 2 of this section.

8. To demonstrate compliance with 12 VAC 5-590-420 subdivisions E 1 through E 4 of this section, a waterworks owner shall report to the appropriate field office the information specified in 12 VAC 5-590-530 D 5.

F. Lead public education requirements. The owner of a waterworks that exceeds the lead action level based on tap water samples collected in accordance with 12 VAC 5-590-370 B 6 a shall deliver the public education materials contained in 12 VAC 5-590-420 subdivisions F 1 and F 2 of this section in accordance with the requirements in 12 VAC 5-590-420 subdivision F 3 of this section.

1. Content of written materials. A waterworks owner shall include the following text in all of the printed materials distributed through the lead public education program. Any additional information presented by the owner shall be consistent with the information below and be in plain English that can be understood by laypersons.

a. Introduction. The United States Environmental Protection Agency (EPA) and (insert name of waterworks) are concerned about lead in your drinking water. Although most homes have very low levels of lead in their drinking water, some homes in the community have lead levels above the EPA action level of 15 parts per billion (ppb), or 0.015 milligrams of lead per liter of water (mg/L). Under Federal law we are required to have a program in place to minimize lead in your drinking water by (insert date when corrosion control will be completed for your waterworks). This program includes corrosion control treatment, source water treatment, and public education. We are also required to replace each lead service line that we control if the line contributes lead concentrations of more than 15 ppb after we have completed the comprehensive treatment program. If you have any questions about how we are carrying out the requirements of the lead regulation please give us a call at (insert waterworks phone number). This brochure explains the simple steps you can take to protect you and your family by reducing your exposure to lead in drinking water.

b. Health effects of lead. Lead is a common metal found throughout the environment in lead-based paint, air, soil, household dust, food, certain types of pottery porcelain and pewter, and water. Lead can pose a significant risk to your health if too much of it enters your body. Lead builds up in the body over many years and can cause damage to the brain, red blood cells and kidneys. The greatest risk is to young children and pregnant women. Amounts of lead that will not hurt adults can slow down normal mental and physical development of growing bodies. In addition, a child at play often comes into contact with sources of lead contamination like dirt and dust that rarely affect an adult. It is important to wash children's hands and toys often, and to try to make sure they only put food in their mouths.

c. Lead in drinking water.

(1) Lead in drinking water, although rarely the sole cause of lead poisoning, can significantly increase a person's total lead exposure, particularly the exposure of infants who drink baby formulas and concentrated juices that are mixed with water. The EPA estimates that drinking water can make up 20% or more of a person's total exposure to lead.

(2) Lead is unusual among drinking water contaminants in that it seldom occurs naturally in water supplies like rivers and lakes. Lead enters drinking water primarily as a result of the corrosion, or wearing away, of materials containing lead in the water distribution system and household plumbing. These materials include lead-based solder used to join copper pipe, brass and chrome plated brass faucets, and in some cases, pipes made of lead that connect your house to the water main (service lines). In 1986, Congress banned the use of lead solder containing greater than 0.2% lead, and restricted the lead content of faucets, pipes and other plumbing materials to 8.0%.

(3) When water stands in lead pipes or plumbing systems containing lead for several hours or more, the lead may dissolve into your drinking water. This means the first water drawn from the tap in the morning, or later in the afternoon after returning from work or school, can contain fairly high levels of lead.

d. Steps you can take in the home to reduce exposure to lead in drinking water.

(1) Despite our best efforts mentioned earlier to control water corrosivity and remove lead from the water supply, lead levels in some homes or buildings can be high. To find out whether you need to take action in your own home, have your drinking water tested to determine if it contains excessive concentrations of lead. Testing the water is essential because you cannot see, taste, or smell lead in drinking water. Some local laboratories that can provide this service are listed at the end of this booklet. (The waterworks owners should contact the Division of Consolidated Laboratory Service at (804) 786-3411 for a list of certified laboratories in their area). For more information on having your water tested, please call (insert phone number of waterworks).

(2) If a water test indicates that the drinking water drawn from a tap in your home contains lead above 15 ppb, then you should take the following precautions:

(a) Let the water run from the tap before using it for drinking or cooking any time the water in a faucet has gone unused for more than six hours. The longer water resides in your home's plumbing the more lead it may contain. Flushing the tap means running the cold water faucet until the water gets noticeably colder, usually about 15-30 seconds. If your house has a lead service line to the water main, you may have to flush the water for a longer time, perhaps one minute, before drinking. Although toilet flushing or showering flushes water through a portion of your home's plumbing system, you still need to flush the water in each faucet before using it for drinking or cooking. Flushing tap water is a simple and inexpensive measure you can take to protect your family's health. It usually uses less than one or two gallons of water and costs less than (insert a cost estimate based on flushing two times a day for 30 days) per month. To conserve water, fill a couple of bottles for drinking water after flushing the tap, and whenever possible use the first flush water to wash the dishes or water the plants. If you live in a high-rise building, letting the water flow before using it may not work to lessen your risk from lead. The plumbing systems have more, and sometimes larger pipes than smaller buildings. Ask your landlord for help in locating the source of the lead and for advice on reducing the lead level.

(b) Try not to cook with, or drink water from the hot water tap. Hot water can dissolve more lead more quickly than cold water. If you need hot water, draw water from the cold tap and heat it on the stove or microwave.

(c) Remove loose lead solder and debris from the plumbing materials installed in newly constructed homes, or homes in which the plumbing has recently been replaced, by removing the faucet strainers from all taps and running the water from 3 three to 5 five minutes. Thereafter, periodically remove the strainers and flush out any debris that has accumulated over time.

(d) If your copper pipes are joined with lead solder that has been installed illegally since it was banned in 1986, notify the plumber who did the work and request that he or she replace the lead solder with lead-free solder. Lead solder looks dull gray, and when scratched with a key looks shiny. In addition, notify the local building official in your city or county.

(e) Determine whether or not the service line that connects your home or apartment to the water main is made of lead. The best way to determine if your service line is made of lead is by either hiring a licensed plumber to inspect the line or by contacting the plumbing contractor who installed the line. You can identify the plumbing contractor by checking your localities' record of building permits which should be maintained in the files of the (insert name of department that issues building permits). A licensed plumber can at the same time check to see if your home's plumbing contains lead solder, lead pipes, or pipe fittings that contain lead. The waterworks that delivers water to your home should also maintain records of the materials located in the distribution system. If the service line that connects your dwelling to the water main contributes more than 15 ppb to drinking water, after our comprehensive treatment program is in place, we are required to replace the line. Since the line is only partially controlled by the (insert name of the city, county, or waterworks that controls the line), we are required to provide you with information on how to replace your portion of the service line, and offer to replace that portion of the line at your expense and take a follow-up tap water sample within 14 days of the replacement. Acceptable replacement alternatives include copper, steel, iron, and plastic pipes and must comply with local plumbing codes.

(f) Have an electrician check your wiring. If grounding wires from the electrical system are attached to your pipes, corrosion may be greater. Check with a licensed electrician or your local electrical code to determine if your wiring can be grounded elsewhere. DO NOT attempt to change the wiring yourself because improper grounding can cause electrical shock and fire hazards.

(3) The steps described above will reduce the lead concentrations in your drinking water. However, if a water test indicates that the drinking water coming from your tap contains lead concentrations in excess of 15 ppb after flushing, or after we have completed our actions to minimize lead levels, then you may want to take the following additional measures.

(a) Purchase or lease a home treatment device. Home treatment devices are limited in that each unit treats only the water that flows from the faucet to which it is connected, and all of the devices require periodic maintenance and replacement. Devices such as reverse osmosis systems or distillers can effectively remove lead from your drinking water. Some activated carbon filters may reduce lead levels at the tap, however all lead reduction claims should be investigated. Be sure to check the actual performance of a specific home treatment device before and after installing the unit.

(b) Purchase bottled water for drinking and cooking.

(4) You can consult a variety of sources for additional information. Your family doctor or pediatrician can perform a blood test for lead and provide you with information about the health effects of lead. State and local government agencies that can be contacted include:

(a) (Insert the name of the waterworks) at (insert phone number) can provide you with information about your community's waterworks and a list of local laboratories that have been certified by Division of Consolidated Laboratory Services for testing water quality.

(b) (Insert the name of city or county department that issues building permits) at (insert phone number) can provide you with information about building permit records that should contain the names of plumbing contractors that plumbed your home.

(c) The Medical Director of (Insert the name of the city or county) Health Department, and the Virginia Department of Health Division of Maternal and Child Health, Lead Programs Director at 1-800-523-4019 can provide you with information about the health effects of lead and how you can have your child's blood tested.

(5) The following is a list of some state-approved laboratories in your area that you can call to have your water tested for lead. (Insert names and phone numbers of at least two laboratories.)

2. Content of broadcast materials. A waterworks owner shall include the following information in all public service announcements submitted under the lead public education program to television and radio stations for broadcasting:

a. Why should everyone want to know the facts about lead and drinking water? Because unhealthy amounts of lead can enter drinking water through the plumbing in your home. That's why I urge you to do what I did. I had my water tested for (insert free or $ per sample). You can contact the (insert the name of the waterworks) for information on testing and on simple ways to reduce your exposure to lead in drinking water.

b. To have your water tested for lead, or to get more information about this public health concern, please call (insert the phone number of the waterworks).

3. Delivery of a public education program.

a. In communities where a significant proportion of the population speaks a language other than English, public education materials shall be communicated in the appropriate language(s).

b. The owner of a community waterworks that fails to meet the lead action level on the basis of tap water samples collected in accordance with 12 VAC 5-590-370 B 6 a shall, within 60 days:

(1) Insert notices in each customer's water utility bill containing the information in 12 VAC 5-590-420 subdivision F 1 of this section, along with the following alert on the water bill itself in large print: "SOME HOMES IN THIS COMMUNITY HAVE ELEVATED LEAD LEVELS IN THEIR DRINKING WATER. LEAD CAN POSE A SIGNIFICANT RISK TO YOUR HEALTH. PLEASE READ THE ENCLOSED NOTICE FOR FURTHER INFORMATION."

(2) Submit the information in 12 VAC 5-590-420 subdivision F 1 of this section to the editorial departments of the major daily and weekly newspapers circulated throughout the community.

(3) Deliver pamphlets and/or brochures that contain the public education materials in 12 VAC 5-590-420 subdivisions F 1 b and 12 VAC 5-590-420 F 1 d of this section to facilities and organizations, including the following:

(a) Public schools and/or local school boards;

(b) City or county health department;

(c) Women, Infants, and Children and/or Head Start Program(s) whenever available;

(d) Public and private hospitals and/or clinics;

(e) Pediatricians;

(f) Family planning clinics; and

(g) Local welfare agencies.

(4) Submit the public service announcement in 12 VAC 5-590-420 subdivision F 2 of this section to at least five of the radio and television stations with the largest audiences that broadcast to the community served by the waterworks.

c. The owner of a community waterworks shall repeat the tasks contained in 12 VAC 5-590-420 subdivisions F 3 b (1), (2), and (3) of this section every 12 months, and the tasks contained in 12 VAC 5-590-420 subdivision F 3 b (4) of this section every six months for as long as the waterworks exceeds the lead action level.

d. Within 60 days after it exceeds the lead action level, the owner of a nontransient noncommunity waterworks shall deliver the public education materials contained in 12 VAC 5-590-420 subdivisions F 1 a, b, and d of this section as follows:

(1) Post informational posters on lead in drinking water in a public place or common area in each of the buildings served by the waterworks, and

(2) Distribute informational pamphlets and/or brochures on lead in drinking water to each person served by the nontransient noncommunity waterworks.

e. The owner of a nontransient noncommunity waterworks shall repeat the tasks contained in 12 VAC 5-590-420 subdivision F 3 d of this section at least once during each calendar year in which the waterworks exceeds the lead action level.

f. A waterworks owner may discontinue delivery of public education materials if the waterworks has met the lead action level during the most recent six-month monitoring period conducted pursuant to 12 VAC 5-590-370 B 6 a. The owner shall recommence public education in accordance with this section if the waterworks subsequently exceeds the lead action level during any monitoring period.

4. Supplemental monitoring and notification of results. The owner of a waterworks that fails to meet the lead action level on the basis of tap samples collected in accordance with 12 VAC 5-590-370 B 6 a shall offer to sample the tap water of any customer who requests it. The owner is not required to pay for collecting or analyzing the sample, nor is the owner required to collect and analyze the sample itself.

G. Beginning January 1, 1993, each waterworks owner shall certify annually in writing to the commissioner (using third party or manufacturer's certification) that, when polymers containing acrylamide or epichlorohydrin are used by the waterworks in drinking water systems, the combination (or product) of dose and monomer level does not exceed the following specified levels: Acrylamide = 0.05% dosed at 1 ppm (or equivalent) of polymer. Epichlorohydrin = 0.01% dosed at 20 ppm (or equivalent) of polymer. Certifications may rely on manufacturers or third parties, as approved by the commissioner.

H. Treatment technique for control of disinfection byproduct (DBPP) precursors.

1. Applicability.

a. Waterworks that use surface water or groundwater under the direct influence of surface water using conventional filtration treatment must operate with enhanced coagulation or enhanced softening to achieve the TOC percent removal levels specified in subdivision H 2 of this section unless the waterworks meets at least one of the alternative compliance criteria listed in subdivision H 1 b or c of this section.

b. Alternative compliance criteria for enhanced coagulation and enhanced softening waterworks. Waterworks that use surface water or groundwater under the direct influence of surface water provided with conventional filtration treatment may use the alternative compliance criteria in subdivisions H 1 b (1) through (6) of this section to comply with this section in lieu of complying with subdivision H 2 of this section. Waterworks must still comply with monitoring requirements in 12 VAC 5-590-370 B 3 j.

(1) The waterworks’ source water TOC level, measured according to 12 VAC 5-590-440, is less than 2.0 mg/L, calculated quarterly as a running annual average.

(2) The waterworks’ treated water TOC level, measured according to 12 VAC 5-590-440, is less than 2.0 mg/L, calculated quarterly as a running annual average.

(3) The waterworks’ source water TOC level, measured according to 12 VAC 5-590-440, is less than 4.0 mg/L, calculated quarterly as a running annual average; the source water alkalinity, measured according to 12 VAC 5-590-440, is greater than 60 mg/L (as CaCO3), calculated quarterly as a running annual average; and either the TTHM and HAA5 running annual averages are no greater than 0.040 mg/L and 0.030 mg/L, respectively; or prior to the effective date for compliance in 12 VAC 590-370 B 3 b, the waterworks has made a clear and irrevocable financial commitment not later than the effective date for compliance in 12 VAC 590-370 B 3 b to use of technologies that will limit the levels of TTHMs and HAA5 to no more than 0.040 mg/L and 0.030 mg/L, respectively. Waterworks must submit evidence of a clear and irrevocable financial commitment, in addition to a schedule containing milestones and periodic progress reports for installation and operation of appropriate technologies, to the commissioner for approval not later than the effective date for compliance in 12 VAC 590-370 B 3 b. These technologies must be installed and operating not later than June 30, 2005. Failure to install and operate these technologies by the date in the approved schedule will constitute a violation of these regulations.

(4) The TTHM and HAA5 running annual averages are no greater than 0.040 mg/L and 0.030 mg/L, respectively, and the waterworks uses only chlorine for primary disinfection and maintenance of a residual in the distribution system.

(5) The waterworks’ source water SUVA, prior to any treatment and measured monthly according to 12 VAC 5-590-440, is less than or equal to 2.0 L/mg-m, calculated quarterly as a running annual average.

(6) The waterworks' finished water SUVA, measured monthly according to 12 VAC 5-590-440, is less than or equal to 2.0 L/mg-m, calculated quarterly as a running annual average.

c. Additional alternative compliance criteria for softening waterworks. Waterworks practicing enhanced softening that cannot achieve the TOC removals required by subdivision H 2 b of this section may use the alternative compliance criteria in subdivisions H 1 c (1) and of this section in lieu of complying with subdivision H 2 of this section. Waterworks must still comply with monitoring requirements in 12 VAC 5-590-370 B 3 f (1).

(1) Softening that results in lowering the treated water alkalinity to less than 60 mg/L (as CaCO3), measured monthly according to 12 VAC 5-590-440 and calculated quarterly as a running annual average.

(2) Softening that results in removing at least 10 mg/L of magnesium hardness (as CaCO3), measured monthly and calculated quarterly as an annual running average.

2. Enhanced coagulation and enhanced softening performance requirements.

a. Waterworks must achieve the percent reduction of TOC specified in subdivision H 2 b of this section between the source water and the combined filter effluent, unless the commissioner approves a waterworks’ request for alternate minimum TOC removal (Step 2) requirements under subdivision H 2 c of this section.

b. Required Step 1 TOC reductions, indicated in the following table, are based upon specified source water parameters measured in accordance with 12 VAC 5-590-440. Waterworks practicing softening are required to meet the Step 1 TOC reductions in the far-right column (Source water alkalinity greater than 120 mg/L) for the specified source water TOC:

| Step 1 Required Removal of TOC by Enhanced Coagulation and Enhanced Softening for Community or Nontransient Noncommunity Waterworks That Use Surface Water or Groundwater Under the Direct Influence of Surface Water Using Conventional Treatment 1,2 |
| --- |
| Source-water TOC, mg/L | Source-water alkalinity, mg/L as CaCO3 |
|  | 0-60 | (60-120 | >120 3 |
| >2.0-4.0 | 35.0% | 25.0% | 15.0% |
| >4.0-8.0 | 45.0% | 35.0% | 25.0% |
| >8.0 | 50.0% | 40.0% | 30.0% |

1Waterworks meeting at least one of the conditions in subdivisions H 1 b (1) through (6) of this section are not required to operate with enhanced coagulation.

2Softening waterworks meeting one of the alternative compliance criteria in subdivision H 1 c of this section are not required to operate with enhanced softening.

3Waterworks practicing softening must meet the TOC removal requirements in this column.

c. Waterworks that use surface water or groundwater under the direct influence of surface water with conventional treatment systems that cannot achieve the Step 1 TOC removals required by subdivision H 2 b of this section due to water quality parameters or operational constraints must apply to the commissioner, within three months of failure to achieve the TOC removals required by subdivision H 2 b of this section, for approval of alternative minimum TOC (Step 2) removal requirements submitted by the waterworks. If the commissioner approves the alternative minimum TOC removal (Step 2) requirements, the commissioner may make those requirements retroactive for the purposes of determining compliance. Until the commissioner approves the alternate minimum TOC removal (Step 2) requirements, the waterworks must meet the Step 1 TOC removals contained in subdivision H 2 b of this section.

d. Alternate minimum TOC removal (Step 2) requirements. Applications, made to the commissioner by waterworks using enhanced coagulation, for approval of alternative minimum TOC removal (Step 2) requirements under subdivision H 2 c of this section must include, at a minimum, results of bench- or pilot-scale testing conducted under subdivision H 2 d (1) of this section. The submitted bench- or pilot-scale testing must be used to determine the alternate enhanced coagulation level.

(1) Alternate enhanced coagulation level is defined as coagulation at a coagulant dose and pH as determined by the method described in subdivisions H 2 d (1) through (5) of this section such that an incremental addition of 10 mg/L of alum (or equivalent amount of ferric salt) results in a TOC removal of equal to or less than 0.3 mg/L. The percent removal of TOC at this point on the “TOC removal versus coagulant dose” curve is then defined as the minimum TOC removal required for the waterworks. Once approved by the commissioner, this minimum requirement supersedes the minimum TOC removal required by the table in subdivision H 2 b of this section. This requirement will be effective until such time as the commissioner approves a new value based on the results of a new bench- and pilot-scale test. Failure to achieve the alternative minimum TOC removal levels set by the commissioner is a violation of these regulations.

(2) Bench- or pilot-scale testing of enhanced coagulation must be conducted by using representative water samples and adding 10 mg/L increments of alum (or equivalent amounts of ferric salt) until the pH is reduced to a level less than or equal to the enhanced coagulation Step 2 target pH shown in the following table:

| Enhanced Coagulation Step 2 target pH |
| --- |
| Alkalinity (mg/L as CaCO3) | Target pH |
| 0-60 | 5.5 |
| >60-120 | 6.3 |
| >120-240 | 7.0 |
| >240 | 7.5 |

(3) For waters with alkalinities of less than 60 mg/L for which addition of small amounts of alum or equivalent addition of iron coagulant drives the pH below 5.5 before significant TOC removal occurs, the waterworks must add necessary chemicals to maintain the pH between 5.3 and 5.7 in samples until the TOC removal of 0.3 mg/L per 10 mg/L alum added (or equivalent addition of iron coagulant) is reached.

(4) The waterworks may operate at any coagulant dose or pH necessary (consistent with other sections of these regulations) to achieve the minimum TOC percent removal approved under subdivision H 2 c of this section.

(5) If the TOC removal is consistently less than 0.3 mg/L of TOC per 10 mg/L of incremental alum dose at all dosages of alum (or equivalent addition of iron coagulant), the water is deemed to contain TOC not amenable to enhanced coagulation. The waterworks may then apply to the commissioner for a waiver of enhanced coagulation requirements.

3. Compliance calculations.

a. Waterworks that use surface water or groundwater under the direct influence of surface water other than those identified in subdivision H 1 b or H 1 c of this section must comply with requirements contained in subdivision H 2 b or H 2 c of this section. Waterworks must calculate compliance quarterly, beginning after the waterworks has collected 12 months of data, by determining an annual average using the following method:

(1) Determine actual monthly TOC percent removal, equal to:

(1((treated water TOC/source water TOC))(100

(2) Determine the required monthly TOC percent removal (from either the table in subdivision H 2 b of this section or from subdivision H 2 c of this section).

(3) Divide the value in subdivision H 3 a (1) of this section by the value in subdivision H 3 a (2) of this section.

(4) Add together the results of subdivision H 3 a (3) of this section for the last 12 months and divide by 12.

(5) If the value calculated in subdivision H 3 a (4) of this section is less than 1.00, the waterworks is not in compliance with the TOC percent removal requirements.

b. Waterworks may use the provisions in subdivisions H 3 b (1) through (5) of this section in lieu of the calculations in subdivisions H 3 a (1) through (5) of this section to determine compliance with TOC percent removal requirements.

(1) In any month that the waterworks’ treated or source water TOC level, measured according to 12 VAC 5-590-440, is less than 2.0 mg/L, the waterworks may assign a monthly value of 1.0 (in lieu of the value calculated in subdivision H 3 a (3) of this section) when calculating compliance under the provisions of subdivision H 3 a of this section.

(2) In any month that a waterworks practicing softening removes at least 10 mg/L of magnesium hardness (as CaCO3), the waterworks may assign a monthly value of 1.0 (in lieu of the value calculated in subdivision H 3 a (3) of this section) when calculating compliance under the provisions of subdivision H 3 a of this section.

(3) In any month that the waterworks’ source water SUVA, prior to any treatment and measured according to 12 VAC 5-590-440, is equal to or less than 2.0 L/mg-m, the waterworks may assign a monthly value of 1.0 (in lieu of the value calculated in subdivision H 3 a (3) of this section) when calculating compliance under the provisions of subdivision H 3 a of this section.

(4) In any month that the waterworks’ finished water SUVA, measured according to 12 VAC 5-590-440, is equal to or less than 2.0 L/mg-m, the waterworks may assign a monthly value of 1.0 (in lieu of the value calculated in subdivision H 3 a (3) of this section) when calculating compliance under the provisions of subdivision H 3 a of this section.

(5) In any month that a waterworks practicing enhanced softening lowers alkalinity below 60 mg/L (as CaCO3), the waterworks may assign a monthly value of 1.0 (in lieu of the value calculated in subdivision H 3 a (3) of this section) when calculating compliance under the provisions of subdivision H 3 a of this section.

c. Waterworks that use surface water or groundwater under the direct influence of surface water and using conventional treatment may also comply with the requirements of this section by meeting the criteria in subdivision H 1 b or H 1 c of this section.

4. Enhanced coagulation or enhanced softening is the treatment technique required to control the level of DBP precursors in drinking water treatment and distribution systems for waterworks using surface water or groundwater under the direct influence of surface water and using conventional treatment.

I. The best technology, treatment techniques, or other means available for achieving compliance with the maximum contaminant levels for disinfection byproducts show in Table 2.13 are listed below:

1. Enhanced coagulation or enhanced softening or GAC10, with chlorine as the primary and residual disinfectant is the best available technology for achieving compliance with the maximum contaminant level for TTHM or HAA5.

2. Control of ozone treatment process to reduce production of bromate is the best available technology for achieving compliance with the maximum contaminant level for bromate.

3. Control of treatment processes to reduce disinfectant demand and control of disinfection treatment processes to reduce disinfectant levels is the best available technology for achieving compliance with the maximum contaminant level for chlorite.

4. A waterworks that is installing GAC or membrane technology to comply with Table 2.13 may apply to the commissioner for an extension of up to 24 months past the dates in 12 VAC 5-590-370 B 3 b, but not beyond December 31, 2003. In granting the extension, the commissioner must set a schedule for compliance and may specify any interim measures that the waterworks must take. Failure to meet the schedule or interim treatment requirements constitutes a violation of 12 VAC 5-590-410.

J. The best technology, treatment techniques, or other means available for achieving compliance with the maximum residual disinfectant levels identified in Table 2.12 is the control of treatment processes to reduce disinfectant demand and control of disinfection treatment processes to reduce disinfectant levels.

12 VAC 5-590-440. Analytical methods.

Analytical methods to determine compliance with the requirements of this chapter shall be those specified in the applicable edition of Standard Methods for the Examination of Water and Wastewater, published by the American Public Health Association, the American Water Works Association, and the Water Pollution Control Federation; "Methods for Chemical Analysis of Water and Wastes," Environmental Protection Agency, Office of Technology Transfer, Washington, D.C. 20460, 1974; and "Methods for the Determination of Organic Compounds in Finished Drinking Water and Raw Source Water" (Sept 1986), EPA, Environmental Monitoring and Support Laboratory, Cincinnati, OH 45268 or in the case of primary maximum contaminant levels, those methods shall be followed by the Division of Consolidated Laboratory Services and consistent with current U.S. Environmental Protection Agency regulations found at 40 CFR Part 141 (1991). All laboratories seeking certification to perform drinking water analyses must comply with 1 VAC 30-40-10 et seq. promulgated by the Department of General Services, Division of Consolidated Laboratory Services.

| Table 2.2 Inorganic Chemicals. |
| --- |
| Substance | Primary Maximum Contaminant Level (mg/L) |
| Antimony | 0.006 |
| Arsenic (As) | 0.05 |
| Asbestos | 7 Million Fibers/Liter (longer than 10 um) |
| Barium (Ba) | 2 |
| Beryllium | 0.004 |
| Cadium (Cd) | 0.005 |
| Chromium (Cr) | 0.1 |
| Cyanide (as free Cyanide) | 0.2 |
| Fluoride (F) | 4.0 # |
| Mercury (Hg) | 0.002 |
| Nickel | 0.1 |
| Nitrate (as N) | 10** |
| Nitrite (as N) | 1 |
| Total Nitrate and Nitrite (as N) | 10 |
| Selenium (Se) | 0.05 |
| Thallium | 0.002 |
| Substance | Secondary Maximum Contaminant Level (mg/L) |
| Chloride (Cl) | 250.0 |
| Corrosivity | Non-Corrosive, See Appendix B |
| Fluoride | 2.0 |
| Foaming Agents | 0.5* |
| Iron (Fe) | 0.3 |
| Manganese (Mn) | 0.05 |
| Sodium (Na) | No Limits Designated |
| Sulfate (SO4) | 250.0 |
| Zinc (Zn) | 5.0 |
| Substance | Action Level (mg/L) |
| Lead (Pb) | 0.015 |
| Copper (Cu) | 1.3 |

# Note. For artificially fluoridated waterworks the minimum concentration of fluoride should be 0.8 mg/L and the maximum should be 1.0 mg/L. The optimum control limit is 0.9 mg/L. (See Appendix B)

* Note. Concentration reported in terms of Methylene Blue Active Substances.

**Note. See Appendix B for Exception Regarding Noncommunity Waterworks.

| Table 2.3 Organic Chemicals. |
| --- |
| Substance | Primary Maximum Contaminant Levels (mg/L) |
| VOC |  |
| 1. Vinyl Chloride | 0.002 |
| 2. Benzene | 0.005 |
| 3. Carbon Tetrachloride | 0.005 |
| 4. 1,2-Dichloroethane | 0.005 |
| 5. Trichloroethylene (TCE) | 0.005 |
| 6. 1,1-Dichloroethylene | 0.007 |
| 7. 1,1,1-Trichloroethane | 0.2 |
| 8. para-Dichlorobenzene | 0.075 |
| 9. cis-1,2-Dichloroethylene | 0.07 |
| 10. 1,2-Dichloropropane | 0.005 |
| 11. Ethylbenzene | 0.7 |
| 12. Monochlorobenzene | 0.1 |
| 13. o-Dichlorobenznen | 0.6 |
| 14. Styrene | 0.1 |
| 15. Tetrachloroethylene | 0.005 |
| 16. Toluene | 1 |
| 17. trans-1,2-Dichloroethylene | 0.1 |
| 18. Xylene (total) | 10 |
| 19. Dichloromethane | 0.005 |
| 20. 1,2,4-Trichlorobenzene | 0.07 |
| 21. 1,1,2-Trichloroethane | 0.05 |
| THM |  |
| Total Trihalomethanes | 0.10 |
| SOC |  |
| 1. Alachlor | 0.002 |
| 2. Atrazine | 0.003 |
| 3. Carbofuran | 0.04 |
| 4. Chlordane | 0.002 |
| 5. Heptachlor | 0.0004 |
| 6. Heptachlor epoxide | 0.0002 |
| 7. Polychlorinated biphenyls (PCBs) | 0.0005 |
| 8. Dibromochloropropane (DBCP) | 0.0002 |
| 9. Ethylene dibromide (EDB) | 0.00005 |
| 10. Lindane | 0.0002 |
| 11. Methoxychlor | 0.04 |
| 12. Toxaphene | 0.003 |
| 13. 2,4-Dichlorophenoxyacetic Acid (2,4-D) | 0.07 |
| 14. 2,4,5-Trichlorophenoxypropionic Acid (2,4,5-TP or Silvex) | 0.05 |
| 15. Reserved |  |
| 16. Reserved |  |
| 17. Reserved |  |
| 18. Pentachlorophenol | 0.001 |
| 19. Benzo(a)pyrene | 0.0002 |
| 20. Dalapon | 0.2 |
| 21. Di(2-ethylhexy)adipate | 0.4 |
| 22. Di(2-ethylhexy)phthalate | 0.006 |
| 23. Dinoseb | 0.007 |
| 24. Diquat | 0.02 |
| 25. Endothall | 0.1 |
| 26. Endrin | 0.002 |
| 27. Glyphosate | 0.7 |
| 28. Hexachlorobenzene | 0.001 |
| 29. Hexachlorocyclopentadiene | 0.05 |
| 30. Oxamyl (Vydate) | 0.2 |
| 31. Picloram | 0.5 |
| 32. Simazine | 0.004 |
| 33. 2,3,7,8-TCDD (Dioxin) | 3 X 10-8 |

| Table 2.4 Physical Quality. |
| --- |
| Parameter | MAXIMUM CONTAMINANT LEVEL | Concentration |
| Color | Secondary | 15 Color Units |
| Odor | Secondary | 3 Threshold odor numbers |
| pH | Secondary | 6.5-8.5 |
| Total Dissolved | Secondary | 500 mg/L Solids (TDS) |
| Turbidity | Primary | *1 Turbidity Unit |

* See Appendix B for operational requirements. The PMCL for turbidity is being phased out of existence. This PMCL will apply to waterworks that filter with surface water sources or groundwater sources under the direct influence of surface water until June 29, 1993. This PMCL will apply to waterworks that do not filter and have surface water sources or groundwater sources under direct influence of surface water until June 29, 1993, or until filtration is installed, whichever is later.

| Table 2.5 Radiological Quality. |
| --- |
| SUBSTANCE | Primary Maximum Contaminant Level |
| A. Total Radium (Radium-226 and Radium-228) | 5 pCi/L |
| B. Gross Alpha Activity (including Radium-226 and excluding Radon and Uranium) | 15 pCi/L |
| Primary Maximum Contaminant Levels for Beta Particle and Photon Radioactivity from Man-Made Radionuclides 1. The average annual concentration of Beta particle and Photon radioactivity from man-made radionuclides in drinking water shall not produce an annual dose equivalent to the total body or any internal organ greater than 4 millirem/year. 2. Except for the radionuclides listed in Schedule I, the concentration of man-made radionuclides causing 4 MREM total body or organ dose equivalents shall be calculated on the basis of a 2 liter per day drinking water intake using the 168 hour data listed in “Maximum Permissible Body Burdens and Water for Occupational Exposure,” MBS Handbook 69 as amended August 1963, U.S. Department of Commerce. If two or more radionuclides are present, the sum of their annual dose equivalent to the total body or to any organ exceed 4 millirem/year. |
| Schedule I Average annual concentrations assumed to produce a total body organ dose of 4 MREM/year. |
| Radionuclide | Critical Organ | pCi/liter |
| Tritium | Total Body | 20,000 |
| Strontium-90 | Bone Marrow | 8 |

*See Appendix B

| Table 2.6 Unregulated Contaminant Organics to be Monitored. |
| --- |
| Group A |
| 1. Chloroform | 12. Chloromethane |
| 2. Bromodichloromethane | 13. Bromoethane |
| 3. Chlorodibromomethane | 14. 1,2,3-Trichloropropane |
| 4. Bromoform | 15. 1,1,1,2-Tetrachloroethane |
| 5. Chlorobenzene | 16. Chloroethane |
| 6. m-Dichlorobenzene | 17. 2,2-Dichloropropane |
| 7. Dibromomethane | 18. o-Chlorotoluene |
| 8. 1,1-Dichloropropene | 19. p-Chlorotoluene |
| 9. 1,1-Dichloroethane | 20. Bromobenzene |
| 10. 1,1,2,2-Tetrachloroethane | 21. 1,3-Dichloropropene |
| 11. 1,3-Dichloropropane |  |
| Group B |
| 1. Aldrin | 8. Metoachlor |
| 2. Butachlor | 9. Metribuzin |
| 3. Carbaryl | 10. Propachlor |
| 4. Dicamba | 11. Aldicarb |
| 5. Dieldrin | 12. Aldicarb sulfone |
| 6. Methomyl | 13. Aldicarb sulfoxide |
| 7. 3-Hyposycarbofuran |  |

Table 2.7 Organic Chemical Monitoring Implementation Schedule Inorganics to be Monitored.

1. Sulfate

| Table 2.8 Organic Chemical Monitoring Implementation Schedule. |
| --- |
| Number of Persons Served | Monitoring to Begin During the Quarter that Begins |
| over 10,000 | January 1, 1988 |
| 3,300 to 10,000 | January 1, 1989 |
| less than 3,300 | January 1, 1991 |

| Table 2.9 PMCL Effective Dates. |
| --- |
| Table 2.3, Organics Chemicals, VOC 1 through 8 (Phase I) | January 9, 1989 |
| Total Trihalomethanes and Fluoride | July 1, 1991 |
| Table 2.3, Organics Chemicals, VOC 9 through 18 and SOC 1 through 14 (Phase II VOCs and SOCs) | July 30, 1992 |
| Asbestos, Cadmium, Chromium, Mercury, Nitrate, Nitrite, Total Nitrate+Nitrite, Selenium (Phase II IOCs) | July 30,1992 |
| Table 2.3, Organics Chemicals, SOC 15 through 18 and Table 2.2, Inorganic Chemicals, Barium (Phase II SOCs and IOCs) | January 1, 1993 |
| Table 2.3, Organics Chemicals, VOC 19 through 21, SOC 19 through 33 and Table 2.2, Inorganic Chemicals; antimony, beryllium, cyanide (as free cyanide), nickel, and thallium | January 17, 1994 |

| Table 2.10 Maximum Contaminant Level Goals for Microbiological Contaminants. |
| --- |
| Contaminant | MCLG |
| Giardia lamblia | zero |
| Viruses | zero |
| Legionella | zero |
| Total coliforms (including fecal coliforms and Escherichia coli) | zero |
| Cryptosporidium | zero |

| Table 2.11 Maximum Contaminant Level Goals for Disinfection Byproducts. |
| --- |
| Disinfection byproduct | MCLG (mg/L) |
| Chloroform | Zero |
| Bromodichloromethane | Zero |
| Bromoform | Zero |
| Bromate | Zero |
| Dichloroacetic acid | Zero |
| Trichloroacetic acid | 0.3 |
| Chlorite | 0.8 |
| Dibromochloromethane | 0.06 |

| Table 2.12 Maximum Residual Disinfectant Level Goals (MRDLG) and Maximum Residual Disinfectant Levels (MRDL) for Disinfectants. |
| --- |
| Disinfectant residual | MRDLG(mg/L) | MRDL (mg/L) |
| Chlorine | 4 (as Cl2). | 4.0 (as Cl2). |
| Chloramines | 4 (as Cl2). | 4.0 (as Cl2) |
| Chlorine dioxide | 0.8 (as ClO2) | 0.8 (as ClO2) |

Notwithstanding the MRDLs in Table 2.12, waterworks may increase residual disinfectant levels in the distribution system of chlorine or chloramines (but not chlorine dioxide) to a level and for a time necessary to protect public health, to address specific microbiological contamination problems caused by circumstances such as, but not limited to, distribution line breaks, storm run-off events, source water contamination events, or cross-connection events.

| Table 2.13 Primary Maximum Contaminant Levels (PMCL) for Disinfection Byproducts |
| --- |
| Disinfection byproduct | Current PMCL1(mg/L) | Future PMCL2(mg/L) |
| Total trihalomethanes (TTHM) | 0.10 | 0.080 |
| Haloacetic acids (five) (HAA5) |  | 0.060 |
| Bromate |  | 0.010 |
| Chlorite |  | 1.0 |

1The primary maximum contaminant level (PMCL) of 0.10 mg/L for total trihalomethanes (the sum of the concentrations of bromodichloromethane, dibromochloromethane, tribromomethane (bromoform), and trichloromethane (chloroform)) applies to community waterworks using surface water or groundwater under the direct influence of surface water that serve a population of 10,000 people or more until December 31, 2001. This level applies to community waterworks that use only groundwater not under the direct influence of surface water and that serve a population of 10,000 people or more until December 31, 2003. Compliance with the primary maximum contaminant level for total trihalomethanes is calculated pursuant to 12 VAC 5-590-370 C 2 b (2) (a) (i). After December 31, 2003, this PMCL is no longer applicable.

2Community or nontransient noncommunity waterworks that use surface water or groundwater under the direct influence of surface water and serving 10,000 or more persons, must comply with this PMCL beginning January 1, 2002. Community or nontransient noncommunity waterworks that use surface water or groundwater under the direct influence of surface water serving fewer than 10,000 persons and waterworks using only groundwater not under the direct influence of surface water must comply with this PMCL beginning January 1, 2004.

12 VAC 5-590-500. Disinfection by chlorination.

A. All water supplies derived from surface water sources in whole or in part shall be disinfected in accordance with 12 VAC 5-590-1000 until June 29, 1993. It is recommended that a chlorine residual be maintained. Beginning June 29, 1993, every owner of a waterworks shall comply with the disinfection requirements of 12 VAC 5-590-420.

B. Waterworks utilizing surface waters as a water supply shall practice prechlorination. The requirement for prechlorination may be waived by the division when warranted.

C. Waterworks utilizing groundwater as a water supply that has been determined by the division to be under the direct influence of surface water, as provided in 12 VAC 5-590-430, will be required to disinfect. If the division determines that the groundwater supply is surface influenced, the waterworks owner shall provide disinfection during the interim before filtration is installed in accordance with 12 VAC 5-590-420 B 2 f. If filtration is installed prior to June 29, 1993, the owner shall comply with the disinfection requirements of 12 VAC 5-590-1000 until June 29, 1993. By June 29, 1993, all waterworks owners using a groundwater source determined to be under the direct influence of surface water must comply with the disinfection requirements of 12 VAC 5-590-420.

D. Any waterworks utilizing groundwater as a water supply that is not governed by 12 VAC 5-590-500 will be required to disinfect in accordance with 12 VAC 5-590-1000 if a sanitary survey reveals a potential source of contamination or if the water fails to meet the bacteriological quality standards set forth in Article 1, (12 VAC 5-590-340 et seq.) of Part II of this chapter.

E. Disinfection profile data and disinfection benchmark data.

1. Any waterworks that has disinfection profile data must retain this data in graphic form, as a spreadsheet, or in some other format acceptable to the commissioner for review as part of sanitary surveys conducted by the commissioner.

2. Disinfection benchmarking.

a. Any waterworks that has developed a disinfection profile and that decides to make a significant change to its disinfection practice must consult with the commissioner prior to making such change. Significant changes to disinfection practice are:

(1) Changes to the point of disinfection;

(2) Changes to the disinfectants used in the treatment plant;

(3) Changes to the disinfection process; and

(4) Any other modification identified by the commissioner.

b. Any waterworks that is modifying its disinfection practice must calculate its disinfection benchmark using the following procedure:

(1) For each year of profiling data collected, the waterworks must determine the lowest average monthly Giardia lamblia inactivation in each year of profiling data. The waterworks must determine the average Giardia lamblia inactivation for each calendar month for each year of profiling data by dividing the sum of daily Giardia lamblia inactivation by the number of values calculated for that month.

(2) The disinfection benchmark is the lowest monthly average value (for waterworks with one year of profiling data) or average of lowest monthly average values (for waterworks with more than one year of profiling data) of the monthly logs of Giardia lamblia inactivation in each year of profiling data.

(3) A waterworks that uses either chloramines or ozone for primary disinfection must also calculate the disinfection benchmark for viruses using a method approved by the commissioner.

c. The waterworks must submit the following information to the commissioner as part of the waterworks’ consultation process.

(1) A description of the proposed change;

(2) The disinfection profile for Giardia lamblia (and, if necessary, viruses) and benchmark listed in subdivision E 2 b of this section; and

(3) An analysis of how the proposed change will affect the current levels of disinfection.

12 VAC 5-590-530. Reporting.

A. The results of any required monitoring activity shall be reported by the waterworks owner to the appropriate field office no later than the 10th day of the month following the month during which the tests were taken.

1. Waterworks required to sample quarterly must report to the appropriate field office within 10 days after the end of each quarter in which samples were collected.

2. Waterworks required to sample less frequently than quarterly must report to the appropriate field office within 10 days after the end of each monitoring period in which samples were collected.

B. It shall be the duty and responsibility of an owner to report to the appropriate field office in the most expeditious manner (usually by telephone) under the following circumstances. If it is done by telephone a confirming report shall be mailed as soon as practical.

1. When a bacteriological examination shows a repeat sample is required (see 12 VAC 5-590-380 D), a report shall be made within 48 hours. A waterworks owner must report a total coliform PMCL violation to the appropriate field office no later than the end of the next business day.

2. When the daily average of turbidity testing exceeds 5 NTU a report shall be made within 48 hours.

3. When a Primary Maximum Contaminant Level of an inorganic or organic chemical is exceeded for a single sample the owner shall report same within seven days. If any one sample result would cause the compliance average to be exceeded the owner shall report same in 48 hours.

4. When the average value of samples collected pursuant to 12 VAC 5-590-410 exceeds the Primary Maximum Contaminant Level of any organic or inorganic chemical the owner shall report same within 48 hours.

5. When the maximum contaminant level for radionuclides has been exceeded as determined by Table 2.5 the results shall be reported within 48 hours.

6. The waterworks owner shall report to the appropriate field office within 48 hours the failure to comply with the monitoring and sanitary survey requirements of this chapter.

7. The waterworks owner shall report to the appropriate field office within 48 hours the failure to comply with the requirements of any schedule prescribed pursuant to a variance or exemption.

C. Reporting requirements for filtration treatment and disinfection treatment.

C. 1. The owner of a waterworks that provides filtration treatment shall report monthly to the division the following specified information beginning June 29, 1993, or when filtration is installed, whichever is later.

1. a. Turbidity measurements as required by 12 VAC 5-590-370 B 7 a shall be reported within 10 days after the end of each month the waterworks serves water to the public. Information that shall be reported includes:

a. (1) The total number of filtered water turbidity measurements taken during the month.

b. (2) The number and percentage of filtered water turbidity measurements taken during the month which are less than or equal to the turbidity limits specified in 12 VAC 5-590-420 B 2 for the filtration technology being used.

c. (3) The date and value of any turbidity measurements taken during the month which exceed 5 NTU.

b. In addition, a waterworks serving at least 10,000 people using surface water or groundwater under the direct influence of surface water that provides conventional filtration treatment or direct filtration must report monthly to the commissioner the information specified in subdivisions C 1 b (1) and (2) of this section beginning January 1, 2002. Also, a waterworks that provides filtration approved under 12 VAC 5-590-420 B 2 d must report monthly to the commissioner the information specified in subdivision C 1 b (1) of this section beginning January 1, 2002. The reporting in subdivision C 1 b (1) of this section is in lieu of the reporting specified in C 1 a.

(1) Turbidity measurements as required by 12 VAC 5-590-420 B 2 a (3) must be reported within 10 days after the end of each month the system serves water to the public. Information that must be reported includes:

(a) The total number of filtered water turbidity measurements taken during the month.

(b) The number and percentage of filtered water turbidity measurements taken during the month that are less than or equal to the turbidity limits specified in 12 VAC 5-590-420 B 2 a (3) or 12 VAC 5-590-420 B 2 d.

(c) The date and value of any turbidity measurements taken during the month that exceed 1 NTU for systems using conventional filtration treatment or direct filtration, or that exceed the maximum level set by the commissioner under 12 VAC 590-420 B 2 d.

(2) Waterworks must maintain the results of individual filter monitoring taken under 12 VAC 5-590-370 B 7 b (1) for at least three years. Waterworks must report that they have conducted individual filter turbidity monitoring under 12 VAC 5-590-370 B 7 b (1) within 10 days after the end of each month the waterworks system serves water to the public. Waterworks must report individual filter turbidity measurement results taken under 12 VAC 5-590-370 B 7 b (1) within 10 days after the end of each month the waterworks serves water to the public only if measurements demonstrate one or more of the conditions in subdivisions C 1 b (2) (a) through (d) of this section. Waterworks that use lime softening may apply to the commissioner for alternative exceedance levels for the levels specified in subdivisions C 1 b (2) (a) through (d) of this section if they can demonstrate that higher turbidity levels in individual filters are due to lime carryover only and not due to degraded filter performance.

(a) For any individual filter that has a measured turbidity level of greater than 1.0 NTU in two consecutive measurements taken 15 minutes apart, the waterworks must report the filter number, the turbidity measurement, and the date, or dates, on which the exceedance occurred. In addition, the waterworks must either produce a filter profile for the filter within seven days of the exceedance (if the waterworks is not able to identify an obvious reason for the abnormal filter performance) and report that the profile has been produced or report the obvious reason for the exceedance.

(b) For any individual filter that has a measured turbidity level of greater than 0.5 NTU in two consecutive measurements taken 15 minutes apart at the end of the first four hours of continuous filter operation after the filter has been backwashed or otherwise taken offline, the waterworks must report the filter number, the turbidity, and the date, or dates, on which the exceedance occurred. In addition, the waterworks must either produce a filter profile for the filter within seven days of the exceedance (if the waterworks is not able to identify an obvious reason for the abnormal filter performance) and report that the profile has been produced or report the obvious reason for the exceedance.

(c) For any individual filter that has a measured turbidity level of greater than 1.0 NTU in two consecutive measurements taken 15 minutes apart at any time in each of three consecutive months, the waterworks must report the filter number, the turbidity measurement, and the date, or dates, on which the exceedance occurred. In addition, the waterworks must conduct a self-assessment of the filter within 14 days of the exceedance and report that the self-assessment was conducted. The self-assessment must consist of at least the following components: assessment of filter performance; development of a filter profile; identification and prioritization of factors limiting filter performance; assessment of the applicability of corrections; and preparation of a filter self-assessment report.

(d) For any individual filter that has a measured turbidity level of greater than 2.0 NTU in two consecutive measurements taken 15 minutes apart at any time in each of two consecutive months, the waterworks must report the filter number, the turbidity measurement, and the date, or dates, on which the exceedance occurred. In addition, the waterworks must arrange for the conduct of a comprehensive performance evaluation by the commissioner or a third party approved by the commissioner no later than 30 days following the exceedance and have the evaluation completed and submitted to the commissioner no later than 90 days following the exceedance.

2. Disinfection information specified below shall be reported to the division within 10 days after the end of each month the waterworks serves water to the public. Information that shall be reported includes:

a. For each day, the lowest measurement of residual disinfectant concentration in mg/L in water entering the distribution system.

b. The date and duration of each period when the residual disinfectant concentration in water entering the distribution system fell below 0.2 mg/L and when the division was notified of the occurrence.

c. The following information on the samples taken in the distribution system in conjunction with total coliform monitoring pursuant to 12 VAC 5-590-420 B.

(1) Number of instances where the residual disinfectant concentration is measured;

(2) Number of instances where the residual disinfectant concentration is not measured but HPC is measured;

(3) Number of instances where the residual disinfectant concentration is measured but not detected and no HPC is measured;

(4) Number of instances where no residual disinfectant concentration is detected and where HPC is greater than 500/mL;

(5) Number of instances where the residual disinfectant concentration is not measured and HPC is greater than 500/mL;

(6) For the current and previous month the system serves water to the public, the value of "V" in percent in the following formula:

V =  c + d + e  x 100

---------

a + b

a = the value in subdivision C 2 c (1) of this section.

b = the value in subdivision C 2 c (2) of this section

c = the value in subdivision C 2 c (3) of this section

d = the value in subdivision C 2 c (4) of this section

e = the value in subdivision C 2 c (5) of this section.

(7) If the division determines, based on site specific considerations, that a waterworks owner has no means for having a sample transported and analyzed for HPC by a certified laboratory within the requisite time and temperature conditions and that the waterworks is providing adequate disinfection in the distribution system, the requirements of 12 VAC 5-590-530 subdivision C 2 c (1) through (6) of this section do not apply.

d. A waterworks owner need not report the data listed in 12 VAC 5-590-530 subdivision C 2 a of this section if all data listed in 12 VAC 5-590-530 subdivisions C 2 a through c of this section remain on file at the waterworks and the division determines that the waterworks owner has submitted all of the information required by 12 VAC 5-590-530 subdivisions C 2 a through c of this section for the last 12 months.

3. Additional reporting requirements.

a. Each waterworks owner, upon discovering that a waterborne disease outbreak potentially attributable to that waterworks has occurred, shall report that occurrence to the division as soon as possible, but no later than by the end of the next business day.

b. If at any time the turbidity exceeds 5 NTU, the waterworks owner shall inform the division as soon as possible, but no later than the end of the next business day.

(1) c. Additional reporting requirements for waterworks serving at least 10,000 people.

(1) If at any time the turbidity exceeds 1 NTU in representative samples of filtered water in a waterworks using conventional filtration treatment or direct filtration, the waterworks must inform the commissioner as soon as possible, but no later than the end of the next business day.

(2) If at any time the turbidity in representative samples of filtered water exceed the maximum level set by the commissioner in 12 VAC 5-590-420 B 2 d for filtration technologies other than conventional filtration treatment, direct filtration, slow sand filtration, or diatomaceous earth filtration, the waterworks must inform the commissioner as soon as possible, but no later than the end of the next business day.

c. If at any time the chlorine residual falls below 0.2 mg/L in the water entering the distribution system, the waterworks owner shall notify the division as soon as possible, but no later than by the end of the next business day. The waterworks owner also shall notify the division by the end of the next business day whether or not the residual was restored to at least 0.2 mg/L within four hours.

D. Reporting requirements for lead and copper. All waterworks owners shall report all of the following information to the appropriate field office in accordance with this section.

1. Reporting requirements for tap water monitoring for lead and copper and for water quality parameter monitoring.

a. A waterworks owner shall report the information specified below for all tap water samples within the first 10 days following the end of each applicable monitoring period specified in 12 VAC 5-590-370 B 6 a, 12 VAC 5-590-370 B 6 b and 12 VAC 5-590-370 B 6 c (i.e., every six months, annually, or every three years).

(1) The results of all tap samples for lead and copper including location or a location site code and the criteria under 12 VAC 5-590-370 B 6 a (1) (c), (d), (e), (f) and/or (g) under which the site was selected for the waterworks' sampling pool;

(2) A certification that each first draw sample collected by the waterworks is one-liter in volume and, to the best of their knowledge, has stood motionless in the service line, or in the interior plumbing of a sampling site, for at least six hours;

(3) Where residents collected samples, a certification that each tap sample collected by the residents was taken after the waterworks owner informed them of proper sampling procedures specified in 12 VAC 5-590-370 B 6 a (2) (b);

(4) The 90th percentile lead and copper concentrations measured from among all lead and copper tap water samples collected during each monitoring period (calculated in accordance with 12 VAC 5-590-410 E 3);

(5) With the exception of initial tap sampling conducted pursuant to 12 VAC 5-590-370 B 6 a (4) (a), the waterworks owner shall designate any site which was not sampled during previous monitoring periods, and include an explanation of why sampling sites have changed;

(6) The results of all tap samples for pH, and where applicable, alkalinity, calcium, conductivity, temperature, and orthophosphate or silica collected under 12 VAC 5-590-370 B 6 b (2) through (5);

(7) The results of all samples collected at the entry point(s) to the distribution system for applicable water quality parameters under 12 VAC 5-590-370 B 6 (2) through (5).

b. By the applicable date in 12 VAC 5-590-370 B 6 a (4) (a) for commencement of monitoring, the owner of each community waterworks which does not complete the targeted sampling pool with tier 1 sampling sites meeting the criteria in 12 VAC 5-590-370 B 6 a (1) (c) shall send a letter to the appropriate field office justifying the selection of tier 2 and/or tier 3 sampling sites under 12 VAC 5-590-370 B 6 a (1) (d) and/or 12 VAC 5-590-370 B 6 a (1) (e).

c. By the applicable date in 12 VAC 5-590-370 B 6 a (4) (a) for commencement of monitoring, the owner of each nontransient, noncommunity waterworks which does not complete the sampling pool with tier 1 sampling sites meeting the criteria in 12 VAC 5-590-370 B 6 a (1) (f) shall send a letter to the appropriate field office justifying the selection of sampling sites under 12 VAC 5-590-370 B 6 a (1) (5).

d. By the applicable date in 12 VAC 5-590-370 B 6 a (4) (a) for commencement of monitoring, the owner of each waterworks with lead service lines that is not able to locate the number of sites served by such lines required under 12 VAC 5-590-370 B 6 a (1) (b) (i) shall send a letter to the appropriate field office demonstrating why the owner was unable to locate a sufficient number of such sites based upon the information listed in 12 VAC 5-590-370 B 6 a (1) (b).

e. Each waterworks owner who requests that the commissioner reduce the number and frequency of sampling shall provide the information required under 12 VAC 5-590-370 B 6 a (4) (d).

2. Water supply (source water) monitoring reporting requirements.

a. A waterworks owner shall report the sampling results for all source water samples collected in accordance with 12 VAC 5-590-370 B 6 c within the first 10 days following the end of each source water monitoring period (i.e., annually, per compliance period, per compliance cycle) specified in 12 VAC 5-590-370 B 6 c.

b. With the exception of the first round of source water sampling conducted pursuant to 12 VAC 5-590-370 B 6 c(2), the waterworks owner shall specify any site which was not sampled during previous monitoring periods, and include an explanation of why the sampling point has changed.

3. Corrosion control treatment reporting requirements. By the applicable dates under 12 VAC 5-590-420 C 2, waterworks owners shall report the following information:

a. For waterworks demonstrating that they have already optimized corrosion control, information required in 12 VAC 5-590-420 C 2 b (2) or 12 VAC 5-590-420 C 2 b (3).

b. For waterworks required to optimize corrosion control, the owner's recommendation regarding optimal corrosion control treatment under 12 VAC 5-590-420 C 1 a.

c. For waterworks required to evaluate the effectiveness of corrosion control treatments under 12 VAC 5-590-420 C 1 c, the information required by that paragraph.

d. For waterworks required to install optimal corrosion control designated by the commissioner under 12 VAC 5-590-420 C 1 d (1), a letter certifying that the owner has completed installing that treatment.

4. Water supply source water treatment reporting requirements. By the applicable dates in 12 VAC 5-590-420 D, waterworks owners shall provide the following information to the appropriate field office:

a. If required under 12 VAC 5-590-420 D 2 a, the owner's recommendation regarding source water treatment;

b. For waterworks required to install source water treatment under 12 VAC 5-590-420 D 2 b, a letter certifying that the waterworks has completed installing the treatment designated by the commissioner within 24 months after the commissioner designated the treatment.

5. Lead service line replacement reporting requirements. Waterworks owners shall report the following information to the appropriate field office to demonstrate compliance with the requirements of 12 VAC 5-590-420 E:

a. Within 12 months after a waterworks exceeds the lead action level in sampling referred to in 12 VAC 5-590-420 E 1, the owner shall demonstrate in writing to the appropriate field office that the owner has conducted a materials evaluation, including the evaluation in 12 VAC 5-590-370 B 6 a(1), to identify the initial number of lead service lines in the distribution system, and shall provide the appropriate field office with the waterworks' schedule for replacing annually at least 7.0% of the initial number of lead service lines in its distribution system.

b. Within 12 months after a waterworks exceeds the lead action level in sampling referred to in 12 VAC 5-590-420 E 1, and every 12 months thereafter, the waterworks owner shall demonstrate to the appropriate field office in writing that the waterworks owner has either:

(1) Replaced in the previous 12 months at least 7.0% of the initial lead service lines (or a greater number of lines specified by the commissioner under 12 VAC 5-590-420 E 6) in the distribution system, or

(2) Conducted sampling which demonstrates that the lead concentration in all service line samples from an individual line(s), taken pursuant to 12 VAC 5-590-370 B 6 a(7)(c), is less than or equal to 0.015 mg/L. In such cases, the total number of lines replaced and/or which meet the criteria in 12 VAC 5-590-420 E 3 shall equal at least 7.0% of the initial number of lead lines identified under paragraph 12 VAC 5-590-512 subdivision D 5 a of this section (or the percentage specified by the commissioner under 12 VAC 5-590-420 E 6).

c. The annual letter submitted to the appropriate field office under 12 VAC 5-590-510 subdivision D 5 b of this section shall contain the following information:

(1) The number of lead service lines scheduled to be replaced during the previous year of the waterworks' replacement schedule;

(2) The number and location of each lead service line replaced during the previous year of the waterworks' replacement schedule;

(3) If measured, the water lead concentration and location of each lead service line sampled, the sampling method, and the date of sampling.

d. As soon as practicable, but in no case later than three months after a waterworks exceeds the lead action level in sampling referred to in 12 VAC 5-590-420 E 1, any waterworks owner seeking to rebut the presumption that it has control over the entire lead service line pursuant to 12 VAC 5-590-420 E 4 shall submit a letter to the appropriate field office describing the legal authority (e.g., state statutes, municipal ordinances, public service contracts or other applicable legal authority) which limits the waterworks owner's control over the service lines and the extent of the waterworks owner's control.

6. Public education program reporting requirements. By December 31st of each year, the owner of any waterworks that is subject to the public education requirements in 12 VAC 5-590-420 F shall submit a letter to the appropriate field office demonstrating that the waterworks owner has delivered the public education materials that meet the content requirements in 12 VAC 5-590-420 F 1 and 12 VAC 5-590-420 F 2 and the delivery requirements in 12 VAC 5-590-420 F 3. This information shall include a list of all the newspapers, radio stations, television stations, facilities and organizations to which the owner delivered public education materials during the previous year. The owner shall submit the letter required by this paragraph annually for as long as it exceeds the lead action level.

7. Reporting of additional monitoring data. The owner of any waterworks which collects sampling data in addition to that required by this subpart shall report the results to the appropriate field office within the first 10 days following the end of the applicable monitoring period under 12 VAC 5-590-370 B 6 a, 12 VAC 5-590-370 B 6 b and 12 VAC 5-590-370 B 6 c during which the samples are collected.

E. Reporting requirements for disinfection byproducts. Waterworks must report the following information in accordance with subsection A of this section. (The field office may choose to perform calculations and determine whether the PMCL was violated, in lieu of having the waterworks report that information):

1. A waterworks monitoring for TTHM and HAA5 under the requirements of 12 VAC 5-590-370 B 3 b on a quarterly or more frequent basis must report:

a. The number of samples taken during the last quarter.

b. The location, date, and result of each sample taken during the last quarter.

c. The arithmetic average of all samples taken in the last quarter.

d. The annual arithmetic average of the quarterly arithmetic averages of this section for the last four quarters.

e. Whether, based on 12 VAC 5-590-390 C 2 b (2), the PMCL was violated.

2. A waterworks monitoring for TTHMs and HAA5 under the requirements of 12 VAC 5-590-370 B 3 b less frequently than quarterly (but at least annually) must report:

a. The number of samples taken during the last year.

b. The location, date, and result of each sample taken during the last monitoring period.

c. The arithmetic average of all samples taken over the last year.

d. Whether, based on 12 VAC 5-590-390 C 2 b (2), the PMCL was violated.

3. A waterworks monitoring for TTHMs and HAA5 under the requirements of 12 VAC 5-590-370 B 3 b less frequently than annually must report:

a. The location, date, and result of the last sample taken.

b. Whether, based on 12 VAC 5-590-390 C 2 b (2), the PMCL was violated.

4. A waterworks monitoring for chlorite under the requirements of 12 VAC 5-590-370 B 3 b must report:

a. The number of entry point samples taken each month for the last three months.

b. The location, date, and result of each sample (both entry point and distribution system) taken during the last quarter.

c. For each month in the reporting period, the arithmetic average of all samples taken in each three sample set taken in the distribution system.

d. Whether, based on 12 VAC 5-590-390 C 2 b (2) (c), the PMCL was violated, in which month and how many times it was violated each month.

5. A waterworks monitoring for bromate under the requirements of 12 VAC 5-590-370 B 3 b must report:

a. The number of samples taken during the last quarter.

b. The location, date, and result of each sample taken during the last quarter.

c. The arithmetic average of the monthly arithmetic averages of all samples taken in the last year.

d. Whether, based on 12 VAC 5-590-390 C 2 b (2) (b), the PMCL was violated.

F. Reporting requirements for disinfectants. Waterworks must report the information specified below in accordance with subsection A of this section. (The field office may choose to perform calculations and determine whether the MRDL was violated, in lieu of having the waterworks report that information):

1. A waterworks monitoring for chlorine or chloramines under the requirements of 12 VAC 5-590-370 B 3 b must report:

a. The number of samples taken during each month of the last quarter.

b. The monthly arithmetic average of all samples taken in each month for the last 12 months.

c. The arithmetic average of all monthly averages for the last 12 months.

d. Whether, based on 12 VAC 5-590-410 C 2 b (3) (a), the MRDL was violated.

2. A waterworks monitoring for chlorine dioxide under the requirements of 12 VAC 5-590-370 B 3 b must report:

a. The dates, results, and locations of samples taken during the last quarter.

b. Whether, based on 12 VAC 5-590-410 C 2 b (3) (b), the MRDL was violated.

c. Whether the MRDL was exceeded in any two consecutive daily samples and whether the resulting violation was acute or nonacute.

G. Reporting requirements for disinfection byproduct precursors and enhanced coagulation or enhanced softening. Waterworks must report the following information in accordance with subsection A of this section. (The field office may choose to perform calculations and determine whether the treatment technique was met, in lieu of having the waterworks report that information):

1. A waterworks monitoring monthly or quarterly for TOC under the requirements of 12 VAC 5-590-370 B 3 b and required to meet the enhanced coagulation or enhanced softening requirements in 12 VAC 5-590-420 H 2 b or 12 VAC 5-590-420 H 2 c must report:

a. The number of paired (source water and treated water) samples taken during the last quarter.

b. The location, date, and results of each paired sample and associated alkalinity taken during the last quarter.

c. For each month in the reporting period that paired samples were taken, the arithmetic average of the percent reduction of TOC for each paired sample and the required TOC percent removal.

d. Calculations for determining compliance with the TOC percent removal requirements, as provided in 12 VAC 5-590-420 H 3 a.

e. Whether the system is in compliance with the enhanced coagulation or enhanced softening percent removal requirements in 12 VAC 5-590-420 H 2 a for the last four quarters.

2. A waterworks monitoring monthly or quarterly for TOC under the requirements of 12 VAC 5-590-370 B 3 b and meeting one or more of the alternative compliance criteria in 12 VAC 5-590-420 H 1 b or 12 VAC 5-590-420 H 1 c must report:

a. The alternative compliance criterion that the system is using.

b. The number of paired samples taken during the last quarter.

c. The location, date, and result of each paired sample and associated alkalinity taken during the last quarter.

d. The running annual arithmetic average based on monthly averages (or quarterly samples) of source water TOC for systems meeting a criterion in 12 VAC 5-590-420 H 1 b (2) or (3) or of treated water TOC for systems meeting the criterion in 12 VAC 5-590-420 H 1 b (2).

e. The running annual arithmetic average based on monthly averages (or quarterly samples) of source water SUVA for systems meeting the criterion in 12 VAC 5-590-420 H 1 b (5) or of treated water SUVA for systems meeting the criterion in 12 VAC 5-590-420 H 1 b (6).

f. The running annual average of source water alkalinity for systems meeting the criterion in 12 VAC 5-590-420 H 1 b (3) and of treated water alkalinity for systems meeting the criterion in 12 VAC 5-590-420 H 1 c (1).

g. The running annual average for both TTHM and HAA5 for systems meeting the criterion in 12 VAC 5-590-420 H 1 b (3) or 12 VAC 5-590-420 H 1 b (4).

h. The running annual average of the amount of magnesium hardness removal (as CaCO3, in mg/L) for systems meeting the criterion in 12 VAC 5-590-420 H 1 c (2).

i. Whether the system is in compliance with the particular alternative compliance criterion in 12 VAC 5-590-420 H 1 b or 12 VAC 5-590-420 H 1 c.

E. H. Reporting of analytical results to the appropriate field office will not be required in instances where the state laboratory performs the analysis and reports same to that office.

F. I. Information to be included on the operation monthly report shall be determined by the division for each waterworks on an individual basis. Appendix G contains suggested monthly operation report requirements.

12 VAC 5-590-540. Public notification (Reference Appendix F for checklist and sample format).

A. It shall be the duty and responsibility of the owner to give public notification under the following circumstances. (See Appendix F for mandatory health effects language.)

1. When any applicable PMCL or MRDL has been exceeded as set forth in 12 VAC 5-590-370.

2. Failure to comply with an applicable treatment technique.

3. Failure to comply with the requirements of any schedule prescribed pursuant to a variance or exemption.

4. Failure to do the prescribed monitoring as required.

5. Failure to comply with an applicable testing procedure as prescribed in 12 VAC 5-590-440.

6. Having been granted or having in effect a variance or exemption from an applicable PMCL.

7. Special public notification requirements for fluoride. Notice of violations of the Primary or Secondary Maximum Contaminant Level for fluoride, notices of variances and exemptions from the Primary Maximum Contaminant Level for fluoride, and notices of failure to comply with variance and exemption schedules for the Primary Maximum Contaminant Level for fluoride shall consist of the public notice in Appendix H plus a description of the nature of the violation and a description of any steps which the waterworks is taking to come into compliance.

8. General lead notification as required by PL 100-572 (LCCA).

a. In addition to the requirements of subdivisions A 1 through 6 of this section, the owner of each community waterworks and each nontransient noncommunity waterworks shall issue notice to persons served by that system that may be affected by lead contamination of their waterworks. The division may require subsequent notices. The owner shall provide notice under this section even if there is no exceedance of the Lead Action Level as defined in 12 VAC 5-590-410 E 1.

b. Notice under subdivision A 8 of this section is not required if the waterworks demonstrates to the division that the waterworks including the residential and nonresidential portions connected to the water system are lead free. For the purposes of this paragraph, the term "lead free" when used with respect to solders and flux refers to solders and flux containing not more than 0.2% lead, and when used with respect to pipes and pipe fittings refers to pipes and pipe fittings containing not more than 8.0% lead.

c. Manner of notice. Notice shall be given to persons served by the waterworks either by (i) three newspaper notices (one for each of three consecutive months) as directed by the division; or (ii) once by mail notice with the water bill or in a separate mailing as directed by the division; or (iii) once by hand delivery. For nontransient noncommunity waterworks, notices may be given by continuous posting. If posting is used, the notice shall be posted in a conspicuous place in the area served by the waterworks and continue for three months as directed by the division.

d. General content of notice. Notices issued under this section shall provide a clear and readily understandable explanation of the potential sources of lead in drinking water, potential adverse health effects, reasonably available methods of mitigating known or potential lead content in drinking water, any steps the waterworks is taking to mitigate lead content in drinking water, and the necessity for seeking alternative water supplies, if any. The notice shall include the mandatory health effects language set out in Appendix F. In addition, each notice shall also include specific advice on how to determine if materials containing lead have been used in homes or the water distribution system and how to minimize exposure to water likely to contain high levels of lead. Each notice shall be conspicuous and shall not contain unduly technical language, unduly small print, or similar problems that frustrate the purpose of the notice. Each notice shall contain the telephone number of the waterworks owner, operator, or designee as a source of additional information regarding the notice. Where appropriate, the notice shall be multilingual; and

9. Availability of unregulated contaminant results. The owner shall notify persons served by the waterworks of the availability of the results of sampling conducted for unregulated contaminants under 12 VAC 5-590-370 B 4 by including a notice in the first set of water bills issued by the waterworks after the receipt of the results or written notice within three months. The notice shall identify a person and the telephone number for information on the monitoring results. For surface water source waterworks which provide this public notice after the first quarter of monitoring, the notice must include a statement that additional monitoring will be conducted for three more quarters with the results available upon request.

B. Tier I. The owner of a waterworks in violation as described in subdivisions A 1, 2, and 3 of this section shall give notice as follows:

1. Newspaper. By publication in a daily newspaper of general circulation in the area served by the system as soon as possible but in no case later than 14 days after the violation or failure. If the area served by a waterworks is not served by a daily newspaper of general circulation, notice shall instead be given by publication in a weekly newspaper of general circulation serving the area; and

2. Mail or hand delivery. By mail delivery (by direct mail or with the water bill) or by hand delivery not later than 45 days after the violation or failure. The division may waive mail or hand delivery if it determines that the owner of the waterworks in violation has corrected the violation or failure within the 45-day period. The division must make the waiver in writing and within the 45-day period; and

3. Imminent health threats. For violations of the PMCLs of contaminants or MRDLs of disinfectants that may pose an acute risk to human health by furnishing a copy of the notice to the radio and television stations serving the area served by the waterworks public water system as soon as possible but in no case later than 72 hours after the violation. The following violations are acute violations:

a. Violation of the bacteriological PMCL.

b. Violation of the nitrate PMCL.

c. Occurrence of a waterborne disease outbreak as determined by the commissioner or the State Epidemiologist in an unfiltered waterworks with a surface source or groundwater source influenced by surface water.

d. Violation of the MRDL for chlorine dioxide as defined in Table 2.12 and determined according to 12 VAC 5-590-410 C 2 b (3) (b) (i).

d. e. Other violations as determined by the division.

4. Long term violations. Following the initial notice given under 12 VAC 5-590-540 subdivisions B 1 or B 2 of this section, the owner must give notice at least once every three months by mail delivery (by direct mail or with the water bill) or by hand delivery, for as long as the violation or failure exists.

5. Exceptions:

a. In lieu of the requirements of 12 VAC 5-590-540 subdivision B 1 of this section, the owner of a community waterworks in an area that is not served by a daily or weekly newspaper of general circulation shall give notice within 14 days after the violation or failure by hand delivery or by continuous posting in conspicuous places within the area served by the waterworks. Posting must continue for as long as the violation or failure exists. Notice by hand delivery must be repeated at least every three months for as long as the violation or failure exists.

b. In lieu of the requirements of 12 VAC 5-590-540 subdivisions B 1 and 12 VAC 5-590-540 B 2 of this section, the owner of a noncommunity waterworks may give notice within 14 days after the violation or failure by hand delivery or by continuous posting in conspicuous places within the area served by the waterworks. Posting must continue for as long as the violation or failure exists. Notice by hand delivery must be repeated at least every three months for as long as the violation or failure exists.

C. Tier II. The owner of a waterworks in violation as described in 12 VAC 5-590-540 subdivisions A 4, 12 VAC 5-590-540 A 5, or 12 VAC 5-590-540 A 6 of this section shall give notice as follows:

1. Within three months of the violation or granting of a variance or exemption by publication in a daily newspaper of general circulation in the area served by the waterworks. If the area served by a waterworks is not served by a daily newspaper of general circulation, notice shall instead be given by publication in a weekly newspaper of general circulation serving the area.

2. For long term violations, the owner shall give notice at least once every three months by mail delivery (by direct mail or with the water bill) or by hand delivery, for as long as the violation exists. Repeat notice of the existence of a variance or exemption must be given every three months for as long as the variance or exemption remains in effect.

3. Exceptions:

a. Community waterworks. In lieu of the requirements of 12 VAC 5-590-540 subdivisions C 1 and 12 VAC 5-590-540 C 2 of this section, the owner of a community waterworks in an area that is not served by a daily or weekly newspaper of general circulation shall give notice, within three months of the violation or granting of the variance or exemption, by hand delivery or by continuous posting in conspicuous places within the area served by the waterworks. Posting must continue for as long as the violation exists or a variance or exemption remains in effect. Notice by hand delivery must be repeated at least every three months for as long as the violation exists or a variance or exemption remains in effect.

b. Noncommunity waterworks. In lieu of the requirements of 12 VAC 5-590-540 subdivisions C 1 and 12 VAC 5-590-540 C 2 of this section, the owner of a noncommunity waterworks shall give notice, within three months of the violation or the granting of the variance or exemption, by hand delivery or by continuous posting in conspicuous places within the area served by the waterworks. Posting must continue for as long as the violation exists, or a variance or exemption remains in effect. Notice by hand delivery must be repeated at least every three months for as long as the violation exists or a variance or exemption remains in effect.

c. Minor violations. In lieu of the requirements of 12 VAC 5-590-540 subdivisions C 1 and 12 VAC 5-590-540 C 2 of this section, the owner of a waterworks, at the discretion of the division, may provide less frequent notice for minor monitoring violations as defined by the division, if approved by EPA. Notice of such violations must be given no less frequently than annually.

D. Notice to new billing units. The owner of a community waterworks must give a copy of the most recent public notice for any outstanding violation of any maximum contaminant level , or any maximum residual disinfectant level, or any treatment technique requirement or any variance or exemption schedule to all new billing units or new hookups prior to or at the time service begins.

E. General contents of public notice. Each notice required by this section must provide a clear and readily understandable explanation of the violation, any potential adverse health effects, the population at risk, the steps that the waterworks is taking to correct such violation, the necessity for seeking alternative water supplies, if any, and any preventive measures the consumer should take until the violation is corrected. Each notice shall be conspicuous and shall not contain unduly technical language, unduly small print, or similar problems that frustrate the purpose of the notice. Each notice shall include the telephone number of the owner, operator, or designee of the waterworks as a source of additional information concerning the notice. Where appropriate, the notice shall be multilingual.

F. Mandatory health effects language. When providing the information on potential adverse health effects required by 12 VAC 5-540-590 subsection E of this section in notices of violations of Maximum Contaminant Levels or treatment techniques requirements, or notices of the granting or the continued existence of exemptions or variances, or notices of failure to comply with a variance or exemption schedule, the owner of a waterworks shall include the language specified in Appendix F as appropriate. If language for a particular contaminant is not specified in Appendix F, this subsection does not apply.

G. Public notification by the division. The division may give notice to the public required by this section on behalf of the owner of the waterworks if the division complies with the requirements of this section. However, the owner of the waterworks remains legally responsible for ensuring that the requirements of this section are met.

H. Within 10 days of completion of each public notice, the waterworks owner shall provide the appropriate field office with a representative copy of each type of notice distributed, published, posted and made available to the consumers or to the media.

12 VAC 5-590-550. Recordkeeping.

All waterworks shall retain within their facilities or at a convenient location near their facilities the following records for the minimum time periods specified:

A. Bacteriological Records - Five years

B. Chemical Analyses - 10 years

C. Individual filter monitoring required under 12 VAC 5-590-530 C 1 b (2) three years; and

C. D. The following information shall be provided for subsections A and B above of this section:

1. Date, place, and time of sampling as well as the name of the person who collected the sample;

2. Identification of sample (e.g., routine, check sample, raw water, other);

3. Date of analysis;

4. Laboratory and/or person responsible for performing analysis;

5. Analytical method/technique used; and

6. Results of the analysis.

D. E. Original records of all sampling data and analyses, reports, surveys, letters, evaluations, schedules, commissioner determinations, and any other information required by 12 VAC 5-590-420 C 1, C and 2, D, E, and F; and 12 VAC 5-590-370 B 6 a, B 6 b, and B 6 c pertaining to lead and copper. Each waterworks owner shall retain the records required by this section for no fewer than 12 years.

E. F. Action taken to correct violations of these regulations - three years after last action with respect to violation involved.

F. G. Copies of reports, summaries, or communications relating to any sanitary surveys performed - 10 years following inspection.

G. H. Variance or exemptions granted (and records related thereto) - five years following expiration of variance or exemption.

H. I. Cross connection control program records - 10 years.

I. J. All waterworks shall retain the following additional records:

1. Plant operational records

2. Water well completion reports

3. As-built engineering plans and specifications of facilities

4. Shop drawings of major equipment

5. Records of equipment repair or replacement

6. Updated map of water distribution system

7. All accident reports

APPENDIX B.
BACKGROUND USED IN DEVELOPING THE CHEMICAL, PHYSICAL AND RADIOLOGICAL LIMITS OF THE DRINKING WATER STANDARDS.

COPPER

ACTION LEVEL - 1.3 mg/L

Copper is an essential and beneficial element in human metabolism. The daily copper requirement for adults has been estimated to be 2.0 mg. Preschool age children require about 0.1 mg daily for normal growth. Copper at high doses has, however, been shown to cause stomach and intestinal distress, liver and kidney damage, and anemia.

A primary source of high concentrations of copper in drinking water is from the internal corrosion of copper plumbing within the home. The EPA has established an action level of 1.3 mg/L of copper in first draw tap sample which may result in public waterworks installing measures to control corrosion.

CORROSION

Corrosion is responsible for many problems in the water distribution system including tuberculation with loss of carrying capacity and increased pumping costs, leaks, main ruptures, discoloration and loss of chlorine residual. The corrosivity of drinking water is a parameter which has not only esthetic and economic significance, but is health significant as well. The products of corrosion having the greatest health significance at the present time, cadmium and lead, are addressed as primary maximum contaminants, but there is also a sufficient basis to include corrosivity as a secondary maximum contaminant level.

Corrosivity is controlled by pH adjustment, the use of chemical stabilizers, or other means which are dependent upon the specific conditions of the water. The two major corrosion indicators utilized in Virginia are the Langelier Index (L.I.) and the Aggressive Index (A.I.). Other indicators also exist. The L.I. and A.I. are determined by utilizing some or all of the following parameters:

· pH

· Calcium Hardness

· Alkalinity

· Temperature

· TDS

All waterworks owners will be notified periodically of the corrosivity of their drinking water by the commissioner, either as L.I., A.I. or other appropriate index. Noncorrosive water should be the goal of each waterworks owner.

Furthermore, EPA requires each owner to be aware of type of materials used in the distribution system (including service connections and household plumbing) such as:

| LEAD | COPPER |
| --- | --- |
| Pipe | Piping |
| Solder | Service Lines |
| Caulking | Household Plumbing |
| Lining of Distribution Mains |  |
| Household Plumbing |  |
| GALVANIZED | Ferrous Piping (cast iron and steel) |
|  | Asbestos Cement Pipe |
| Service Lines | Vinyl Lined Asbestos Cement Pipe |
| Household Plumbing | Coal Tar Lined Pipes |
|  | Plastic Pipe |
|  | Piping |
|  | Service Line |
|  | Household Plumbing |

FLUORIDE

When the fluoride concentration in drinking water is maintained within the recommended ranges of 0.8 mg/L minimum and 1.0 mg/L maximum with the optimum being 0.9 mg/L, the consumer will realize a reduction in dental caries. When supplemental fluoridation is practiced, it is particularly advantageous to maintain a fluoride concentration at or near the optimum. The reduction in dental caries experienced at optimal fluoride concentrations will be diminished by as much as 50% when the concentration is 0.2 mg/L below the optimum. An approval limit slightly higher than the optimum can be tolerated without any mottling of teeth, so where fluorides are native to the water supply, these concentrations are acceptable. Higher levels should be reduced by treatment or blending with other sources lower in fluoride content. The U.S. Environmental Protection Agency has determined that the PMCL for fluoride is 4.0 mg/L based on long term toxicity data. The EPA has also determined that the SMCL for fluoride is 2.0 mg/L based on the potential formation of cosmetically objectionable dental fluorosis as a result of long term exposure. The level of the SMCL was based on a balancing of the beneficial and undesirable effects of fluoride.

FOAMING AGENTS

Foaming is an undesirable property of drinking water because it is esthetically displeasing and therefore should be absent. Because no convenient standardized formability test exists, and because surfactants are one major class of substances that cause foaming, this property is determined indirectly by measuring the anionic surfactant concentration of substances measured by the methylene blue method and should not exceed 0.5 mg/L as methylene blue active substances (MBAS).

NITRATE

Nitrate nitrogen (NO3-N) levels not exceeding 20 mg/L may be allowed in a noncommunity waterworks if the owner demonstrates:

1. Such water will not be available to children under 6 months of age; and

2. There will be continuous posting of the fact that NO3-N levels exceed 10 mg/L and the potential health effects of exposure; and

3. Health officials will be notified annually of NO3-N levels that exceed 10 mg/L; and

4. No adverse health effects will result.

NOTE: Nitrite in water poses a greater health hazard but fortunately it seldom occurs in high concentrations. Waters with nitrite-nitrogen concentrations over 1 mg/L should not be used for infant feedings.

MANMADE RADIONUCLIDES

To determine compliance with Table 2.5, the detection limits shall not exceed the concentrations listed in the following Table.

| DETECTION LIMITS FOR MAN-MADE BETA PARTICLE PHOTON EMITTERS |
| --- |
| RADIONUCLIDE | DETECTION LIMIT |
| Tritium | 1,000 pCi/L |
| Strontium-89 | 10 pCi/L |
| Strontium-90 | 2 pCi/L |
| Iodine-131 | 1 pCi/L |
| Cesium-134 | 10 pCi/L |
| Gross Beta | 4 pCi/L |
| Other radionuclides | 1/10 of the applicable limit |

TURBIDITY

Operational requirement: Conventional water filtration plants utilizing surface waters as a source of supply are capable of producing filtered water with a turbidity consistently less than 0.5 TU 0.1 NTU. Therefore, for water filtration plants the filter effluent turbidity for each filter, before any post-filtration chemical addition, operational limit is 0.5 TU 0.1 NTU.

APPENDIX F.

REGISTRAR'S NOTICE: Due to its length, Appendix F is not being published in its entirety. The following text shows the amendments to paragraph 13 and new paragraphs 76 through 81.

MANDATORY HEALTH EFFECTS LANGUAGE FOR PUBLIC NOTIFICATION OF A VIOLATION OF PMCLs, TREATMENT TECHNIQUE REQUIREMENTS, THE GRANTING OF A VARIANCE OR EXEMPTION, OR SCHEDULE OF A VARIANCE OR EXEMPTION.

...

13. Microbiological Contaminants (for use when there is a violation of the treatment technique requirements for filtration and disinfection in Subpart II of this part 12 VAC 5-590-420). The United States Environmental Protection Agency (EPA) sets drinking water standards and has determined that the presence of microbiological contaminants are a health concern at certain levels of exposure. If water is inadequately treated, microbiological contaminants in that water may cause disease. Disease symptoms may include diarrhea, cramps, nausea, and possibly jaundice, and any associated headaches and fatigue. These symptoms, however, are not just associated with disease-causing organisms in drinking water, but also may be caused by a number of factors other than your drinking water. EPA has set enforceable requirements for treating drinking water to reduce the risk of those adverse health effects. Treatment such as filtering and disinfecting the water removes or destroys microbiological contaminants. Drinking water which is treated to meet EPA requirements is associated with little to none of this risk and should be considered safe.

...

76. Chlorine. The United States Environmental Protection Agency (EPA) sets drinking water standards and has determined that chlorine is a health concern at certain levels of exposure. Chlorine is added to drinking water as a disinfectant to kill bacteria and other disease-causing microorganisms and is also added to provide continuous disinfection throughout the distribution system. Disinfection is required for surface water systems. However, at high doses for extended periods of time, chlorine has been shown to affect blood and the liver in laboratory animals. EPA has set a drinking water standard for chlorine to protect against the risk of these adverse effects. Drinking water that meets this EPA standard is associated with little to none of this risk and should be considered safe with respect to chlorine.

77. Chloramines. The United States Environmental Protection Agency (EPA) sets drinking water standards and has determined that chloramines are a health concern at certain levels of exposure. Chloramines are added to drinking water as a disinfectant to kill bacteria and other disease-causing microorganisms and are also added to provide continuous disinfection throughout the distribution system. Disinfection is required for surface water systems. However, at high doses for extended periods of time, chloramines have been shown to affect blood and the liver in laboratory animals. EPA has set a drinking water standard for chloramines to protect against the risk of these adverse effects. Drinking water that meets this EPA standard is associated with little to none of this risk and should be considered safe with respect to chloramines.

78. Chlorine dioxide. The United States Environmental Protection Agency (EPA) sets drinking water standards and has determined that chlorine dioxide is a health concern at certain levels of exposure. Chlorine dioxide is used in water treatment to kill bacteria and other disease-causing microorganisms and can be used to control tastes and odors. Disinfection is required for surface water systems. However, at high doses, chlorine dioxide-treated drinking water has been shown to affect blood in laboratory animals. Also, high levels of chlorine dioxide given to laboratory animals in drinking water have been shown to cause neurological effects on the developing nervous system. These neurodevelopmental effects may occur as a result of a short-term excessive chlorine dioxide exposure. To protect against such potentially harmful exposures, EPA requires chlorine dioxide monitoring at the treatment plant, where disinfection occurs, and at representative points in the distribution system serving water users. EPA has set a drinking water standard for chlorine dioxide to protect against the risk of these adverse effects.

Note: In addition to the language in this introductory text of paragraph 78, waterworks must include either the language in paragraph 78 i or 78 ii of this appendix. Waterworks with a violation at the treatment plant, but not in the distribution system, are required to use the language in paragraph 78 i of this appendix and treat the violation as a nonacute violation. Waterworks with a violation in the distribution system are required to use the language in paragraph 78. ii. of this appendix and treat the violation as an acute violation.

i. The chlorine dioxide violations reported today are the result of exceedances at the treatment facility only, and do not include violations within the distribution system serving users of this water supply. Continued compliance with chlorine dioxide levels within the distribution system minimizes the potential risk of these violations to present consumers.

ii. The chlorine dioxide violations reported today include exceedances of the EPA standard within the distribution system serving water users. Violations of the chlorine dioxide standard within the distribution system may harm human health based on short-term exposures. Certain groups, including pregnant women, infants, and young children, may be especially susceptible to adverse effects of excessive exposure to chlorine dioxide-treated water. The purpose of this notice is to advise that such persons should consider reducing their risk of adverse effects from these chlorine dioxide violations by seeking alternate sources of water for human consumption until such exceedances are rectified. Local and state health authorities are the best sources for information concerning alternate drinking water.

79. Disinfection byproducts and treatment technique for DBPs. The United States Environmental Protection Agency (EPA) sets drinking water standards and requires the disinfection of drinking water. However, when used in the treatment of drinking water, disinfectants react with naturally occurring organic and inorganic matter present in water to form chemicals called disinfection byproducts (DBPs). EPA has determined that a number of DBPs are a health concern at certain levels of exposure. Certain DBPs, including some trihalomethanes (THMs) and some haloacetic acids (HAAs), have been shown to cause cancer in laboratory animals. Other DBPs have been shown to affect the liver and the nervous system, and cause reproductive or developmental effects in laboratory animals. Exposure to certain DBPs may produce similar effects in people. EPA has set standards to limit exposure to THMs, HAAs, and other DBPs.

80. Bromate. The United States Environmental Protection Agency (EPA) sets drinking water standards and has determined that bromate is a health concern at certain levels of exposure. Bromate is formed as a byproduct of ozone disinfection of drinking water. Ozone reacts with naturally occurring bromide in the water to form bromate. Bromate has been shown to produce cancer in rats. EPA has set a drinking water standard to limit exposure to bromate.

81. Chlorite. The United States Environmental Protection Agency (EPA) sets drinking water standards and has determined that chlorite is a health concern at certain levels of exposure. Chlorite is formed from the breakdown of chlorine dioxide, a drinking water disinfectant. Chlorite in drinking water has been shown to affect blood and the developing nervous system. EPA has set a drinking water standard for chlorite to protect against these effects. Drinking water that meets this standard is associated with little to none of these risks and should be considered safe with respect to chlorite.

VA.R. Doc. No. R02-179; Filed May 13, 2002, 2:52 p.m.