TITLE 20. PUBLIC UTILITIES AND TELECOMMUNICATIONS

STATE CORPORATION COMMISSION

REGISTRAR'S NOTICE: The State Corporation Commission is exempt from the Administrative Process Act in accordance with § 2.2-4002 A 2 of the Code of Virginia, which exempts courts, any agency of the Supreme Court, and any agency that by the Constitution is expressly granted any of the powers of a court of record.

The distribution lists that are referenced as Appendices A and B in the following order are not being published.  However, these lists are available for public inspection at the State Corporation Commission, Document Control Center, Tyler Building, 1st Floor, 1300 East Main Street, Richmond, Virginia 23219, from 8:15 a.m. to 5 p.m., Monday through Friday; or may be viewed at the Virginia Code Commission, General Assembly Building, 2nd Floor, 910 Capitol Street, Richmond, Virginia 23219, during regular office hours.

Title of Regulation:  20 VAC 5-315. Regulations Governing Net Energy Metering (amending 20 VAC 5-315-20, 20 VAC 5-315-30, 20 VAC 5-315-40 and 20 VAC 5-315-90).

Statutory Authority:  §§ 12.1-13, 56-576 and 56-594 of the Code of Virginia.

Public Hearing Date:  A public hearing will be scheduled upon request -- Public comments may be submitted until February 14, 2005.

Agency Contact:  Kara Hart, Attorney, Office of General Counsel, 1300 East Main Street, P.O. Box 1197, Richmond, VA 23218, telephone (804) 371-9671, FAX (804) 371-9240, or e-mail kara.hart@scc.virginia.gov.

Summary:

The proposed amendments (i) change the definition of "renewable fuel generator" by increasing the upper limit for nonresidential customers from 25 kilowatts to 500 kilowatts; (ii) change requirements for the completion of the commission-approved notification form that must be filed by the prospective net metering customer in accordance with 20 VAC 5-315-30 depending on whether the renewable fuel generator has an alternating current capacity of 25 kilowatts or less or an alternating current capacity greater than 25 kilowatts; and (iii) add as a condition of interconnection that the vendor has certified that the renewable fuel generator being installed is in compliance with IEEE Standard 1547.  The proposed amendments also add, in the case of renewable fuel generators with an alternating current capacity greater than 25 kilowatts, certain requirements that must be met before interconnection may occur.   These requirements include electric distribution facilities and customer impact limitations; secondary, service and service entrance limitations; transformer loading limitations; integration with electric distribution company facilities grounding; and balance limitation.  The interconnection form contained in 20 VAC 5-315-90 is also amended.

AT RICHMOND, DECEMBER 23, 2004

COMMONWEALTH OF VIRGINIA ex rel.

STATE CORPORATION COMMISSION

CASE NO. PUE-2004-00060

Ex Parte:  In the matter of amending regulations

governing net energy metering

ORDER FOR NOTICE AND INVITING COMMENTS AND REQUESTS FOR HEARING

On May 25, 2000, the State Corporation Commission ("Commission") adopted Regulations Governing Net Energy Metering, 20 VAC 5-315-10 et seq. ("Net Energy Metering Rules"), pursuant to § 56-594 of the Virginia Electric Utility Restructuring Act, Chapter 23 (§ 56-576 et seq.) of Title 56 of the Code of Virginia ("Restructuring Act"), to permit eligible customer-generators to engage in net energy metering by interconnecting their electrical generating facilities with a utility's electric grid and receiving credit for electricity generated and fed back to the electric grid.

Chapter 827 of the 2004 Acts of Assembly amended § 56-594 of the Restructuring Act to revise the definition of eligible customer-generator.  Eligible customer-generator has been revised to mean a customer that owns and operates an electrical generating facility that, among other things, has a capacity of not more than 10 kW for residential customers and 500 kW for nonresidential customers.  The current Net Energy Metering Rules reflect the previous capacity limit for nonresidential customers of 25 kW.

On June 3, 2004, the Commission entered an Order Establishing Proceeding to amend the Net Energy Metering Rules.  Notice of this proceeding was published in the Virginia Register and in newspapers of general circulation throughout the Commonwealth.  Interested persons were directed to file comments and comments were filed by Appalachian Power Company ("APCO"); Virginia Department of Environmental Quality ("DEQ"); Virginia Electric and Power Company ("Dominion Virginia Power"); Maryland, District of Columbia, Virginia Solar Energy Industries Association ("MDV-SEIA"); and the Virginia Wind Energy Collaborative ("VWEC").  The Staff was directed to investigate the matter and to file a report with the Commission presenting its recommendations.

On August 5, 2004, Dominion Virginia Power filed a motion for leave to file reply comments and for modification of the procedural schedule ("Motion").  The Motion requested the Commission to allow for a work group to be convened before the Staff filed its Report and that the parties be allowed an additional opportunity to comment on the Staff Report.

On August 11, 2004, the Commission entered an Order permitting responses to the Motion, permitting Dominion Virginia Power to reply to those responses, and suspending the procedural schedule.  The Commission received responses from APCO, MDV-SEIA, and VWEC supporting a work group.  On August 27, 2004, Dominion Virginia Power filed a reply renewing its request for a work group to be convened.

On September 17, 2004, the Commission issued an Order finding it appropriate to convene a work group and granting the Motion.  The Staff was directed to convene a work group on October 6, 2004.  The work group was directed to focus on developing amendments to the Net Energy Metering Rules that are essential to implementing the statutory change; in other words, those revisions directly related to increasing the capacity limit for nonresidential customer generators from 25 kW to 500 kW.  The Staff was directed to file a report that included proposed rules and interested parties were afforded the opportunity to comment on the Staff Report.

On November 19, 2004, the Staff filed its report.  The Staff Report notes that APCO, DEQ, Dominion Virginia Power, MDV-SEIA, VWEC, as well as Old Mill Power Company and the Virginia, Maryland & Delaware Association of Electric Cooperatives participated in the work group.  The Staff Report summarizes the proposals made by the various work group participants and indicates how such proposals were incorporated into the proposed rules accompanying the Staff Report as Exhibit A ("Proposed Rules").

Among other things, the Proposed Rules amend the definition of "renewable fuel generator" to reflect the statutory change in capacity limit to 500 kW for nonresidential generators.  Nonresidential generators with capacity in excess of 25 kW must submit notification to the electric distribution provider and/or energy service provider at least 60 days prior to the date of interconnection.  Renewable fuel generators are required to be in compliance with the requirements of IEEE Standard 1547 or its successor.  Additional requirements for interconnection for nonresidential systems with capacity in excess of 25 kW include:  electric distribution facilities and customer impact limitations; secondary, service, and service entrance limitations; transformer loading limitations; integration with electric distribution company facilities grounding; and balance limitations.  The Interconnection Notification form is revised to include a recommendation that a prospective net metering customer contact the electric distribution company prior to making financial commitments to the project.

The Staff declined to incorporate proposals by the work group participants regarding, among other things, application and study fees, increased insurance limits, time-of-use metering, and additional information requirements.  The Staff determined that certain proposals would increase requirements on the class of net metering customers currently subject to the Net Energy Metering Rules, were not essential to implementing the statutory change, required more specific support or evidence to implement, or were too open-ended.

The Staff Report also makes two suggestions to clarify the Net Energy Metering Rules and assure consistency with the Code.  These proposals would not be directly related to increasing the capacity limit for nonresidential customer generators from 25 kW to 500 kW.  The Staff proposes to make clear that the 0.1% limit on the total renewable fuel generator capacity in a customer's electric distribution company's service territory was intended to apply only to renewable fuel generators that net meter, rather than all solar, wind, and hydro generators.  The Staff further proposes to make clear that the phrase "customer's electric distribution company's service territory" applies only to the Virginia portion of the service territory.  The Staff did not include these proposals in the Proposed Rules, but requests the Commission consider such suggestions.

Comments on the Staff Report were received from APCO, which indicates satisfaction with the Proposed Rules, and Dominion Virginia Power, which supports the Staff's Proposed Rules and does not oppose the suggestions made by the Staff for the Commission's consideration.  MDV-SEIA and VWEC MDV-SEIA filed comments providing several additional proposals for amending the Net Energy Metering Rules.  Both MDV-SEIA and VWEC also comment on the prohibition on net metering customer generators using time-of-meters.  MDV-SEIA and VWEC argue that this restriction should be eliminated since the change in the law was intended to encompass larger commercial systems and many such generators are required to be on a time-of-use meter based on their peak load.  Mr. Alden M. Hathaway, who lives in a solar powered home and is net-metered, also filed comments requesting the opportunity to be on a time-of-use meter.

NOW THE COMMISSION, upon consideration of the initial comments filed herein, the work group deliberations, the Staff Report and Proposed Rules, and the comments filed thereto, finds that the attached Proposed Rules should be published in the Virginia Register and that public notice be given.  We will direct interested persons to file written comments on, propose modifications or supplements to, or to request a hearing on the Proposed Rules.  As we have indicated before, this proceeding is intended to consider revisions only directly related to increasing the capacity limit for nonresidential customer generators from 25 kW to 500 kW.  Issues outside the scope of implementing this modification will not be open for consideration.  We ask that interested persons specifically address the issue of time-of-use metering.

Accordingly, IT IS ORDERED THAT:

(1) A copy of this Order and the attached Proposed Rules shall be delivered forthwith to the Registrar of Regulations for publication in the Virginia Register.

(2) On or before January 24, 2005, the Commission's Division of Information Resources shall publish the following notice as classified advertising in newspapers of general circulation throughout the Commonwealth of Virginia:

NOTICE TO THE PUBLIC OF A PROCEEDING

TO AMEND REGULATIONS FOR NET ENERGY METERING

PURSUANT TO § 56-594 OF THE CODE OF VIRGINIA

CASE NO. PUE-2004-00060

On May 25, 2000, the State Corporation Commission ("Commission") adopted Regulations Governing Net Energy Metering, 20 VAC 5-315-10 et seq. ("Net Energy Metering Rules"), pursuant to § 56-594 of the Virginia Electric Utility Restructuring Act, Chapter 23 (§ 56-576 et seq.) of Title 56 of the Code of Virginia ("Restructuring Act"), to permit eligible customer-generators to engage in net energy metering by interconnecting their electrical generating facilities with a utility's electric grid and receiving credit for electricity generated and fed back to the electric grid.

Chapter 827 of the 2004 Acts of Assembly amended § 56-594 of the Restructuring Act to revise the definition of eligible customer-generator.  Eligible customer-generator has been revised to mean a customer that owns and operates an electrical generating facility that, among other things, has a capacity of not more than 10 kW for residential customers and 500 kW for nonresidential customers.  The current Net Energy Metering Rules reflect the previous capacity limit for nonresidential customers of 25 kW.

The Commission established this proceeding and requested comment on how the Net Energy Metering Rules should be amended to implement the legislation.  The Commission convened a work group to facilitate the development of amendments.  Based on the comments previously filed and the deliberations of the work group, the Commission Staff filed a report along with proposed rules.  A copy of the Staff Report and the proposed rules is available for public inspection at the Commission's Document Control Center, Tyler Building, First Floor, 1300 East Main Street, Richmond, Virginia 23219, Monday through Friday, 8:15 a.m. to 5:00 p.m., or may be downloaded from the Commission's website:  http://www.scc.virginia.gov/caseinfo.htm.

The Commission has issued an order in this proceeding directing that on or before February 14, 2005, any interested person may file an original and fifteen (15) copies of any comments on the proposed rules with the Clerk of the Commission at the address set forth below.  Comments should be directly related to increasing the capacity limit for nonresidential customer generators from 25 kW to 500 kW.  The Commission also requests comments on the issue of time-of-use metering.  Interested persons desiring to submit comments electronically may do so by following the instructions available at the Commission's website.

On or before February 14, 2005, any interested person also may file an original and fifteen (15) copies of any requests for hearing on the proposed rules with the Clerk of the Commission at the address set forth below.  Any request for hearing shall state with specificity why the issues raised in the request for hearing cannot be adequately addressed in written comments.  If sufficient request for hearing is not received, the Commission may enter an order based upon the papers filed.  Persons expecting to participate as a respondent in any hearing that may be scheduled shall include with their request for hearing an original and fifteen (15) copies of a notice of participation in accordance with 5 VAC 5-20-80 of the Commission Rules of Practice and Procedure.

All filings in this proceeding shall be directed to Joel H. Peck, Clerk, State Corporation Commission, c/o Document Control Center, P.O. Box 2118, Richmond, Virginia 23218, and shall refer to Case No. PUE-2004-00060.

(3) On or before February 14, 2005, any interested person may comment or request a hearing by filing an original and fifteen (15) copies of such comments or requests with Joel H. Peck, Clerk, State Corporation Commission, c/o Document Control Center, P.O. Box 2118, Richmond, Virginia 23218.  Any request for hearing shall state with specificity why the issues raised in the request for hearing cannot be adequately addressed in written comments.  If a sufficient request for hearing is not received, the Commission may consider the matter and enter an order based upon the papers filed herein.  Interested parties shall refer in their comments or requests to Case No. PUE-2004-00060.  Interested persons desiring to submit comments electronically may do so by following the instructions available at the Commission's website: http://www.scc.virginia.gov/caseinfo.htm.

(4) On or before February 14, 2005, persons filing a request for hearing and expecting to participate as a respondent in any hearing that may be scheduled in this matter shall file an original and fifteen (15) copies of a notice of participation in accordance with 5 VAC 5-20-80 of the Commission Rules of Practice and Procedure.  Interested parties shall refer in their notices to Case No. PUE-2004-00060.  All notices of participation shall be filed with the Clerk of the Commission at the address set forth in Paragraph (4) above.

(5) This matter is continued for further order of the Commission.

AN ATTESTED COPY hereof shall be sent by the Clerk of the Commission to:  All electric cooperatives and electric companies in Virginia as listed on Attachment A to this Order; all persons included on Attachment B to this Order; C. Meade Browder, Jr., Senior Assistant Attorney General, Division of Consumer Counsel, Office of the Attorney General, 900 East Main Street, Richmond, Virginia 23219; and the Commission's Divisions of Economics and Finance and Energy Regulation.

20 VAC 5-315-20. Definitions.

The following words and terms when used in this chapter shall have the following meaning unless the context clearly indicates otherwise:

"Billing period" means, as to a particular customer, the time period between the dates on which the electric distribution company or energy service provider, as the case may be, issues the customer's bills.

"Electric distribution company" means the entity that owns and/or operates the distribution facilities delivering electricity to the net metering customer's premises.

"Energy service provider" means the entity providing electric energy to a net metering customer, either as a tariffed, competitive, or default service pursuant to § 56-585 of the Code of Virginia.

"Net metering customer" means a customer owning and operating a renewable fuel generator under a net metering service arrangement.

"Net metering period" means each successive 12-month period beginning with the first meter reading date following the date of final interconnection of the renewable fuel generator with the electric distribution company's facilities.

"Net metering service" means measuring the difference, over the net metering period between electricity supplied to a net metering customer from the electric grid and the electricity generated and fed back to the electric grid by the net metering customer, using a single meter or, as provided in 20 VAC 5-315-70, additional meters.

"Renewable fuel generator" means an electrical generating facility that:

1. Has an alternating current capacity of not more than 10 kilowatts for residential customers and not more than 25 500 kilowatts for nonresidential customers;

2. Uses as its total fuel source solar, wind, or hydro energy;

3. Is owned and operated by the net metering customer and is located on the customer's premises;

4. Is interconnected and operated in parallel with the electric distribution company's facilities; and

5. Is intended primarily to offset all or part of the net metering customer's own electricity requirements.

20 VAC 5-315-30. Company notification.

A. The prospective net metering customer shall submit a completed commission-approved notification form, as provided in 20 VAC 5-315-90, to the electric distribution company and, if different from the electric distribution company, the energy service provider, according to the following time limits.

1. For a renewable fuel generator with an alternating current capacity of 25 kilowatts or less, the notification form shall be submitted at least 30 days prior to the date the customer intends to interconnect his renewable fuel generator to the electric distribution company's facilities.  A Such net metering customer shall have all equipment necessary to complete the grid interconnection installed prior to such notification.  The electric distribution company shall have 30 days from the date of notification to determine whether the requirements contained in 20 VAC 5-315-40 have been met.  The date of notification shall be considered to be the third day following the mailing of such notification form by the prospective net metering customer.

2. For a renewable fuel generator with an alternating current capacity greater than 25 kilowatts, the notification form shall be submitted at least 60 days prior to the date the customer intends to interconnect his renewable fuel generator to the electric distribution company's facilities.  Such net metering customer shall have all equipment necessary to complete the grid interconnection installed prior to such notification.  Such net metering customer should contact his electric distribution company prior to making financial commitments.  The electric distribution company shall have 60 days from the date of notification to determine whether the requirements contained in 20 VAC 5-315-40 have been met.  The date of notification shall be considered to be the third day following the mailing of such notification form by the prospective net metering customer.

B. Thirty-one days after the date of notification for renewable fuel generators with a rated capacity of 25 kilowatts or less, and 61 days after the date of notification for renewable fuel generators with an alternating current capacity greater than 25 kilowatts, a net metering customer may interconnect his renewable fuel generator and begin operation of said renewable fuel generator unless the electric distribution company or the energy service provider requests a waiver of this requirement under the provisions of 20 VAC 5-315-80, prior to said 31st or 61st day, respectively.  In cases where the electric distribution company or energy service provider requests a waiver, a copy of the request for waiver must be mailed simultaneously by the requesting party to the net metering customer and to the commission's Division of Energy Regulation.

C. The electric distribution company shall file with the commission's Division of Energy Regulation a copy of each completed notification form within 30 days of final interconnection.

20 VAC 5-315-40. Conditions of interconnection.

A. A prospective net metering customer may begin operation of his renewable fuel generator on an interconnected basis when:

1. The net metering customer has properly notified both the electric distribution company and energy service provider (in accordance with 20 VAC 5-315-30) of his intent to interconnect;

2. If required by the electric distribution company's net metering tariff, the net metering customer has installed a lockable, electric distribution company accessible, load breaking manual disconnect switch;

3. A licensed electrician has certified, by signing the commission-approved notification form as provided in 20 VAC 5-315-90, that any required manual disconnect switch has been installed properly and that the renewable fuel generator has been installed in accordance with the manufacturer's specifications as well as all applicable provisions of the National Electrical Code;

4. The vendor has certified, by signing the commission-approved notification form as provided in 20 VAC 5-315-90, that the renewable fuel generator being installed is in compliance with the requirements established by Underwriters Laboratories or other national testing laboratories in accordance with IEEE Standard 1547, Standard for Interconnecting Distributed Resources with Electric Power Systems, July 2003;

5. In the case of static inverter-connected renewable fuel generators with an alternating current capacity in excess of 10 kilowatts, the net metering customer has had the inverter settings inspected by the electric distribution company.  The inspecting electric distribution company may impose a fee on the net metering customer of no more than $50 for such inspection;

6. In the case of nonstatic inverter-connected renewable fuel generators, the net metering customer has interconnected according to the electric distribution company's interconnection guidelines and the electric distribution company has inspected all protective equipment settings.  The inspecting electric distribution company may impose a fee on the net metering customer of no more than $50 for such inspection.

7. In the case of renewable fuel generators with an alternating current capacity greater than 25 kilowatts, the following requirements shall be met before interconnection may occur:

a. Electric distribution facilities and customer impact limitations.  A renewable fuel generator shall not be permitted to interconnect to distribution facilities if the interconnection would reasonably lead to damage to any of the electric distribution company's facilities or would reasonably lead to voltage regulation or power quality problems at other customer revenue meters due to the incremental effect of the generator on the performance of the electric distribution system, unless the customer reimburses the electric distribution company for its cost to modify any facilities needed to accommodate the interconnection.

b. Secondary, service, and service entrance limitations.  The capacity of the renewable fuel generator shall be less than the capacity of the electric distribution company-owned secondary, service, and service entrance cable connected to the point of interconnection, unless the customer reimburses the electric distribution company for its cost to modify any facilities needed to accommodate the interconnection.

c. Transformer loading limitations.  The renewable fuel generator shall not have the ability to overload the electric distribution company transformer, or any transformer winding, beyond manufacturer or nameplate ratings, unless the customer reimburses the electric distribution company for its cost to modify any facilities needed to accommodate the interconnection.

d. Integration with electric distribution company facilities grounding.  The grounding scheme of the renewable fuel generator shall comply with IEEE 1547, Standard for Interconnecting Distributed Resources with Electric Power Systems, July 2003, and the electric distribution company shall assist the net metering customer in selecting a grounding scheme that coordinates with its distribution system.

e. Balance limitation.  The renewable fuel generator shall not create a voltage imbalance of more than 3.0% at any other customer's revenue meter if the electric distribution company transformer, with the secondary connected to the point of interconnection, is a three-phase transformer, unless the customer reimburses the electric distribution company for its cost to modify any facilities needed to accommodate the interconnection.

B. A prospective net metering customer shall not be allowed to interconnect a renewable fuel generator if doing so will cause the total rated generating alternating current capacity of all interconnected renewable fuel generators within that customer's electric distribution company's service territory to exceed 0.1% of that company's Virginia peak-load forecast for the previous year.  In any case where a prospective net metering customer has submitted a notification form required by 20 VAC 5-315-30 and that customer's interconnection would cause the total rated generating alternating current capacity of all interconnected renewable fuel generators within that electric distribution company's service territory to exceed 0.1% of that company's Virginia peak-load forecast for the previous year, the electric distribution company shall, at the time it becomes aware of the fact, send written notification to such prospective net metering customer and to the commission's Division of Energy Regulation that the interconnection is not allowed.  In addition, upon request from any customer, the electric distribution company shall provide to the customer the amount of capacity still available for interconnection pursuant to § 56-594 D of the Code of Virginia.

C. Neither the electric distribution company nor the energy service provider shall impose any charges upon a net metering customer for any interconnection requirements specified by this chapter, except as provided under subdivisions A 5 and 6 of this section, and 20 VAC 5-315-50 as related to off-site metering.

20 VAC 5-315-90. Commission-approved interconnection notification form.

The following commission-approved interconnection notification form shall be used as specified in this chapter.

# Appendix A

# Effective 7/2000 11/2004

# INTERCONNECTION NOTIFICATION 1

PURSUANT TO COMMISSION REGULATION 20 VAC 5-315-30, APPLICANT HEREBY GIVES NOTICE OF INTENT TO OPERATE A GENERATING FACILITY.

### Section 1. Applicant Information

Name:  _________________________________________________________________________________________________

Mail Address:  ________________________________________________________________________________________

City: _________________________________________________  State:  ___________     Zip Code:  ____________________

Facility Location  (if different from above):   ___________________________________________________________________

Daytime Phone Number: __________________________________

Distribution Utility:  _____________________________________________  Account Number :  ________________________

Energy Service Provider (ESP):  ___________________________________  Account Number : _________________________

(if  different than electric distribution company)

# Proposed Interconnection Date: ____________________________

# Section 2. Generating Facility Information

Generator Type (check one):   Solar _______,        Wind  _______,     Hydro  _______

Generator Manufacturer, Model Name & Number:  ____________________________________________________________

__________________________________________   Power Rating in Kilowatts: AC:  ______________  DC: _____________

Inverter Manufacturer, Model Name & Number:  ______________________________________________________________

________________________________________________         Battery Backup?  (yes or no)   _______________

Section 3.  Installation Information

Installation Date:_____________________________ Proposed Interconnection Date:  _________________________

Section 3. Information for Renewable Fuel Generators with an Alternating Current Capacity in Excess of 25 Kilowatts

Type (____inverter, ____ induction, ____ synchronous), frequency ____Hz, number of phases _____,

Capacity: DC power ___, AC apparent power ___, AC real power ___, power factor ___%, AC voltage ___, AC amperage__

Facility schematic and equipment layout must be attached to this form.

Section 4.  Certifications Vendor Certification

1.  The system hardware is listed by Underwriters Laboratories to be in compliance with UL 1741:

Signed (Vendor):  _____________________________________________________________      Date:   ________________

Name (printed):  _________________________________________________________    Company:   __________________

# Phone Number:  ___________________________

Section 5. Electrician Certification

2.  The system has been installed in accordance with the manufacturer's specifications as well as all applicable provisions of the National Electrical Code.

Signed (Licensed Electrician): _________________________________________________   Date: _____________________

# License Number: ____________________________________  Phone Number:  _____________________________________

Mail Address:  __________________________________________________________________________________________

City:  _________________________________________________  State:  __________     Zip Code:  ____________________

3.  Utility signature signifies only receipt of this form, in compliance with the Commission's net energy metering regulations, Regulation 20 VAC 5-315-30.

Signed (Utility Representative):  _________________________________________________      Date:  __________________

I hereby certify that, to the best of my knowledge, all of the information provided in this NOtice Notice is true and correct.

Signature of Applicant  ______________________________________________________________

1  Prospective net metering customers considering installing a renewable fuel generator with a capacity in excess of 25 kilowatts are strongly encouraged to contact his electric distribution company prior to making financial commitments to the project.

DOCUMENTS INCORPORATED BY REFERENCE

1547, IEEE Standard for Interconnecting Distributed Resources with Electric Power Systems, July 2003, The Institute of Electrical and Electronics Engineers, Inc.

VA.R. Doc. No. R05-105; Filed January 4, 2005, 4:14 p.m.