TITLE 20. PUBLIC UTILITIES AND TELECOMMUNICATIONS

STATE CORPORATION COMMISSION

REGISTRAR'S NOTICE: The State Corporation Commission is exempt from the Administrative Process Act in accordance with § 2.2-4002 A 2 of the Code of Virginia, which exempts courts, any agency of the Supreme Court, and any agency that by the Constitution is expressly granted any of the powers of a court of record.

Title of Regulation:  20 VAC 5-315. Regulations Governing Net Energy Metering (amending 20 VAC 5-315-20, 20 VAC 5-315-30 and 20 VAC 5-315-40; repealing 20 VAC 5-315-90).

Statutory Authority:  §§ 12.1-13, 56-576 and 56-594 of the Code of Virginia.

Effective Date: April 26, 2005.

Agency Contact:  Kara Hart, Attorney, Office of General Counsel, State Corporation Commission, 1300 East Main Street, P.O. Box 1197, Richmond, VA 23218, telephone (804) 371-9671, FAX (804) 371-9240, or e-mail kara.hart@scc.virginia.gov.

Summary:

The final regulations change the definition of "renewable fuel generator" by increasing the upper limit for nonresidential customers from 25 kilowatts to 500 kilowatts.  The final amendments require a renewable fuel generator with capacity greater than 25 kilowatts to notify the electric distribution company at least 60 days prior to the date of intended interconnection.  The electric distribution company has 60 days from the date notified to determine whether the interconnection conditions have been met.  Also for renewable fuel generators with at least 25 kilowatts in capacity, the final amendments include electric distribution facilities and customer impact limitations; secondary, service and service entrance limitations; transformer loading limitations; integration with electric distribution company facilities grounding; and balance limitations.  As an additional interconnection condition, the vendor must now certify that the renewable fuel generator being installed is in compliance with IEEE Standard 1547.

The following amendments are made to the proposed regulations. The final regulations state that the renewal fuel generator's grounding scheme must be consistent with that of the electric distribution company and that, upon request, the electric distribution company shall assist prospective customer-generators in selecting a coordinating scheme.  The final regulations specify that "renewable fuel generator" means an electrical generating facility that is interconnected pursuant to a net metering arrangement with an electric distribution company's facilities.  They also clarify that the 0.1% limit on the total renewable fuel generator capacity in each Virginia electric distribution company's service territory is intended to apply only to renewable fuel generators that net meter and only to the Virginia portion of the service territory.  Finally, 20 VAC 5-315-90 is repealed and the commission-approved notification form is moved to the forms section of the regulation.

AT RICHMOND, APRIL 20, 2005

COMMONWEALTH OF VIRGINIA ex rel.

STATE CORPORATION COMMISSION

CASE NO. PUE-2004-00060

Ex Parte:  In the matter of amending regulations

governing net energy metering

ORDER ADOPTING FINAL REGULATIONS

Chapter 827 of the 2004 Acts of Assembly amended § 56-594 of the Virginia Electric Utility Restructuring Act, Chapter 23 (§ 56-576 et seq.) of Title 56 of the Code of Virginia ("Restructuring Act"), which permits eligible customer-generators to engage in net energy metering by interconnecting their electrical generating facilities with a utility's electric grid and receiving credit for electricity generated and fed back to the electric grid.  The 2004 General Assembly revised the definition of eligible customer-generator to mean, among other things, a nonresidential customer that owns and operates an electrical generating facility that has a capacity of not more than 500 kW.  The current Regulations Governing Net Energy Metering, 20 VAC 5-315-10 et seq. ("Net Energy Metering Rules") reflect the original 25 kW capacity limit for nonresidential customers.

On June 3, 2004, the Commission entered an Order Establishing Proceeding to amend the Net Energy Metering Rules.  Notice of this proceeding was published in the Virginia Register of Regulations and in newspapers of general circulation throughout the Commonwealth.  Interested persons were directed to file any comments and requests for hearing on the revision of the definition of a customer-generator and how the capacity increase may otherwise need to be reflected in the Net Energy Metering Rules.

Appalachian Power Company ("APCO"); the Virginia Department of Environmental Quality ("DEQ"); Virginia Electric and Power Company ("Virginia Power"); the Maryland, District of Columbia, Virginia Solar Energy Industries Association ("MDV-SEIA"); and the Virginia Wind Energy Collaborative ("VWEC") filed comments on or before the July 19, 2004, deadline.

On August 5, 2004, Virginia Power filed a motion requesting leave to file reply comments and a modification of the procedural schedule, as well as the convening of a work group prior to the filing of the Staff Report and an opportunity to comment on the Staff Report ("Motion").

Ultimately, after receiving responses to the Motion and a reply from Virginia Power renewing its request for a work group, on September 17, 2004, the Commission issued an Order granting the Motion.  The Commission directed the Staff to convene a work group on October 6, 2004, to focus on developing amendments to the Net Energy Metering Rules that are essential to increasing the capacity limit for nonresidential customer generators from 25 kW to 500 kW.  The Staff was directed to file a report that included proposed rules and interested parties were afforded the opportunity to comment on the Staff Report.

On November 19, 2004, the Staff filed its report.  The Staff Report noted that APCO, DEQ, Virginia Power, MDV-SEIA, VWEC, as well as Old Mill Power Company and the Virginia, Maryland & Delaware Association of Electric Cooperative participated in the work group.  Based on the deliberations of the work group, the Staff drafted proposed rules ("Proposed Rules") which were included in the Staff Report.  Among other things, the Proposed Rules amend the definition of "renewable fuel generator" to reflect the statutory change in capacity limit to 500 kW for nonresidential generators; require nonresidential renewable fuel generators with capacity in excess of 25 kW to submit notification to the electric distribution provider or energy service provider at least 60 days prior to the date of interconnection; and require all renewable fuel generators to be in compliance with the requirements of  IEEE Standard 1547.  Additional requirements for interconnection for nonresidential customer-generator systems with capacity in excess of 25 kW include: electric distribution facilities and customer impact limitations; secondary, service, and service entrance limitations; transformer loading limitations; integration with electric distribution company facilities grounding; and balance limitations.  The Interconnection Notification form is revised to include a recommendation that a prospective net metering customer contact the electric distribution company prior to making financial commitments to the project.

The Staff Report made two suggestions, which although not directly related to increasing the capacity limit for nonresidential customer-generators to 500 kW, clarify the Net Energy Metering Rules and assure consistency with the Code.  The Staff proposed to make clear in 20 VAC 5-315-40 that the 0.1% limit on the total renewable fuel generator capacity in each electric distribution company's service territory was intended to apply only to renewable fuel generators that net meter and only to the Virginia portion of the service territory.  The Staff did not include these proposals in the Proposed Rules, but requested that the Commission consider the suggestions.

In addition, the Staff Report indicated that the work group discussed permitting currently prohibited time-of-use metering by net metering customers, but that no resolution was reached on the issue by the work group.  Therefore, the Staff made no recommendation on reversing the prohibition against time-of-use metering.

On December 9, 2004, Mr. Alden M. Hathaway, who lives in a solar powered home and is net-metered, filed comments requesting the opportunity to be on a time-of-use rate schedule.

On December 10, 2004, comments on the Staff Report were received from APCO, Virginia Power, MDV-SEIA, and VWEC.  APCO indicated satisfaction with the Proposed Rules.  Virginia Power supported the Proposed Rules and did not oppose the Staff suggestions for clarification.  In comments and in the work group, MDV-SEIA had argued that the restriction on time-of-use metering contained in the current Net Metering Rules should be eliminated.  The Proposed Rules do not eliminate the prohibition and MDV-SEIA again asserted that such prohibition should be eliminated.  In addition, MDV-SEIA suggested that the definition of net-metered customer should be amended to include a customer who leases its renewable fuel generating equipment.  VWEC generally supported the Proposed Rules, but requested the elimination of the time-of-use prohibition and suggested changes in the definition of renewable fuel generator and the language pertaining to the grounding requirements for renewable fuel generators with capacity in excess of 25 kW.

On December 23, 2004, the Commission issued an Order for Notice and Inviting Comments and Requests for Hearing.  The Proposed Rules were published in the Virginia Register of Regulations and in newspapers of general circulation throughout the Commonwealth.  Interested persons were directed to file any comments and requests for hearing on or before February 14, 2005.  The Commission specifically requested comments on the issue of time-of-use net metering.

On February 14, 2005, APCO filed a letter stating that it did not intend to file additional comments or to request a hearing.  Also on February 14, 2005, Virginia Power filed a letter stating that it did not request a hearing and that it continued to support its comments filed December 10, 2004.

On February 15, 2005, Allegheny Power late-filed comments supporting the Proposed Rules and asserting that there is no conflict between the rule prohibiting time-of-use metering and the increase in capacity for nonresidential customer generators.

On March 2, 2005, MDV-SEIA filed additional comments on the issue of time-of-use metering and requested leave to file such comments out-of-time.  MDV-SEIA argues, among other things, that the prohibition on time-of-use metering thwarts the intent of the Restructuring Act and the Net Energy Metering Rules.

On March 10, 2005, the Commission issued an Order Permitting Response and Reply accepting the late-filed comments and permitting the parties to the proceeding and the Staff to file any response to the filings by Allegheny Power, MDV-SEIA, and VWEC on or before March 24, 2005.

On March 24, 2005, APCO filed a response stating that time-of-use metering is not a proper subject for this proceeding and that the issue should not be considered on the basis of late-filed comments with limited time for reply comment.  APCO suggested consideration of time-of-use metering in a separate proceeding.  In addition, APCO asserted that MDV-SEIA

misinterprets APCO's tariffs and stated that its customers with loads in excess of 25 kW are not required to have time-of-use meters.

Also on March 24, 2005, Virginia Power filed a response first arguing that the elimination of the prohibition on time-of-use customers participating in net metering is outside the scope of implementing the legislative change as directed by the Commission in this proceeding.  Virginia Power stated that the increased capacity threshold should not impact the rule prohibiting time-of-use metering and that the time-of-use prohibition is not necessarily contrary to the public interest.  Virginia Power further asserted that there are unresolved issues and that net metering on time-of-use rates for a large customer is extremely problematic and an administrative nightmare.  In addition, Virginia Power argued that time-of-use net metering would require either two standard meters or one special bidirectional time-of-use meter, and that the customer should pay for any resulting increased metering and billing costs.  Finally, Virginia Power indicated that it may better for the Commission to take a wait-and-see approach.  Virginia Power asserted that other market options for customers with renewable systems are being developed and that the Committee on Electric Utility Restructuring ("CEUR") was recently appropriated money for a study to determine whether the purported benefits of increased use of renewable energy resources to generate electricity in Virginia outweigh the predicted increased costs, compared to the status quo.

As permitted by the Commission's March 24, 2005, Order Granting Motion for an extension, the Staff filed its response on March 28, 2005, noting that time-of-use metering was given limited consideration in the last rulemaking.  The Staff stated its belief that arguments for the elimination of the time-of-use prohibition on net metering customer-generators are reasonable and, conceptually, have public interest merit.  However, the Staff expressed its continuing concerns about the complexities and costs associated with metering and billing for time-of-use customer-generators.  The Staff indicated that it now understands that time-of-use net metering may not necessarily require two meters as it may be possible to set up an electronic meter to act in a bidirectional manner, but that it would be necessary to determine who would be responsible for the costs associated with the special programming, maintenance, and inventory management for such meter.  The Staff argued that issue should be fully explored, with the participation of interested parties, prior to the Commission making a definitive finding.

NOW THE COMMISSION, upon consideration of the record and the applicable law, is of the opinion and finds that the regulations attached hereto as Appendix A should be adopted.  As described herein, the regulations we adopt contain several modifications to the Proposed Rules contained in our December 23, 2004, Order.

The Commission has incorporated the suggestion to clarify that the 0.1% limit on the total renewable fuel generator capacity in an electric distribution company's service territory applies only to renewable fuel generators that are net metered.  The phrase "pursuant to a net metering arrangement" has been added to the definition of renewable fuel generator such that the term means, among other things, an electrical generating facility that is interconnected pursuant to a net metering arrangement governed by these rules and operated in parallel with the electric distribution company's facilities.  In addition, the word Virginia has been added to the phrase "customer's electric distribution company's Virginia service territory" to clarify that the 0.1% limitation applies only to the Virginia portion of the electric distribution company's service territory.  We also adopt the proposed language indicating that the grounding scheme of the renewable fuel generator shall be consistent with the scheme used by the electric distribution company and that, upon a customer's request, the electric distribution company shall assist a prospective net metering customer in selecting a proper scheme.

We will not at this time open a new investigation to explore time-of-use issues with respect to net metering.  As noted above, this proceeding was initiated to implement a specific legislative change and it is not clear that the elimination of the prohibition on time-of-use net metering is essential to implementing such change.  In addition, the CEUR has approved a study by the Virginia Center for Coal and Energy Research at Virginia Tech, which will include recommendations regarding incentives to promote the use of renewable energy and may address the issue of time-of-use net metering.  We agree that it may be premature for the Commission to initiate an investigation into substantive modifications of the net metering program prior to the conclusion of such study.

Accordingly, IT IS ORDERED THAT:

1) The Regulations Governing Net Energy Metering are hereby adopted as shown in Attachment A to this Order.

(2) copy of this Order and the Regulations Governing Net Energy Metering shall be delivered forthwith to the Registrar of Regulations for publication in the Virginia Register of Regulations.

(3) On or before June 15, 2005, all electric utilities in the Commonwealth subject to Chapter 10 (§ 56-232 et seq.) of Title 56 of Code of Virginia shall file with the Commission's Division of Energy Regulation revised tariff provisions necessary to implement the regulations as adopted herein.

(4) There being nothing further to come before the Commission, this case shall be removed from the docket and the papers filed herein be placed in the file for ended causes.

AN ATTESTED COPY hereof shall be sent by the Clerk of the Commission to:  Alden Hathaway, ICF Consulting Group, 9300 Lee Highway, Fairfax, Virginia 22031-1207; Peter Lowenthal, Executive Director, Maryland, District of Columbia Solar Energy Association, 4707 Elmhirst Lane, Bethesda, Maryland 20184-3954; Salud Layton, Esquire, Old Dominion Electric Cooperative, P.O. Box 2340, Glen Allen, Virginia 23058; Michel A. King, President, Old Mill Power Company, 103 Shale Place, Charlottesville, Virginia 22902; Anthony J. Gambardella, Esquire, Woods Rogers P.L.C., 823 East Main Street, Suite 1200, Richmond, Virginia 23219; Karen L. Bell, Esquire, Virginia Electric and Power Company, P.O. Box 26532, Richmond, Virginia 23261; C. Meade Browder, Jr., Senior Assistant Attorney General, Division of Consumer Counsel, Office of Attorney General, 900 East Main Street, 2nd Floor, Richmond, Virginia 23219; and the Commission's Office of General Counsel and Divisions of Public Utility Accounting and Energy Regulation.

20 VAC 5-315-20. Definitions.

The following words and terms when used in this chapter shall have the following meaning unless the context clearly indicates otherwise:

"Billing period" means, as to a particular customer, the time period between the dates on which the electric distribution company or energy service provider, as the case may be, issues the customer's bills.

"Electric distribution company" means the entity that owns and/or operates the distribution facilities delivering electricity to the net metering customer's premises.

"Energy service provider" means the entity providing electric energy to a net metering customer, either as a tariffed, competitive, or default service pursuant to § 56-585 of the Code of Virginia.

"Net metering customer" means a customer owning and operating a renewable fuel generator under a net metering service arrangement.

"Net metering period" means each successive 12-month period beginning with the first meter reading date following the date of final interconnection of the renewable fuel generator with the electric distribution company's facilities.

"Net metering service" means measuring the difference, over the net metering period between electricity supplied to a net metering customer from the electric grid and the electricity generated and fed back to the electric grid by the net metering customer, using a single meter or, as provided in 20 VAC 5-315-70, additional meters.

"Renewable fuel generator" means an electrical generating facility that:

1. Has an alternating current capacity of not more than 10 kilowatts for residential customers and not more than 25 500 kilowatts for nonresidential customers;

2. Uses as its total fuel source solar, wind, or hydro energy;

3. Is owned and operated by the net metering customer and is located on the customer's premises;

4. Is interconnected [ pursuant to a net metering arrangement ] and operated in parallel with the electric distribution company's facilities; and

5. Is intended primarily to offset all or part of the net metering customer's own electricity requirements.

20 VAC 5-315-30. Company notification.

A. The prospective net metering customer shall submit a completed commission-approved notification form [ , as provided in 20 VAC 5-315-90, ] to the electric distribution company and, if different from the electric distribution company, [ to ] the energy service provider, according to the following time limits.

1. For a renewable fuel generator with an alternating current capacity of 25 kilowatts or less, the notification form shall be submitted at least 30 days prior to the date the customer intends to interconnect his renewable fuel generator to the electric distribution company's facilities.  A Such net metering customer shall have all equipment necessary to complete the grid interconnection installed prior to such notification.  The electric distribution company shall have 30 days from the date of notification to determine whether the requirements contained in 20 VAC 5-315-40 have been met.  The date of notification shall be considered to be the third day following the mailing of such notification form by the prospective net metering customer.

2. For a renewable fuel generator with an alternating current capacity greater than 25 kilowatts, the notification form shall be submitted at least 60 days prior to the date the customer intends to interconnect his renewable fuel generator to the electric distribution company's facilities.  Such net metering customer shall have all equipment necessary to complete the grid interconnection installed prior to such notification.  Such net metering customer should contact his electric distribution company prior to making financial commitments.  The electric distribution company shall have 60 days from the date of notification to determine whether the requirements contained in 20 VAC 5-315-40 have been met.  The date of notification shall be considered to be the third day following the mailing of such notification form by the prospective net metering customer.

B. Thirty-one days after the date of notification for renewable fuel generators with a rated capacity of 25 kilowatts or less, and 61 days after the date of notification for renewable fuel generators with an alternating current capacity greater than 25 kilowatts, a net metering customer may interconnect his renewable fuel generator and begin operation of said renewable fuel generator unless the electric distribution company or the energy service provider requests a waiver of this requirement under the provisions of 20 VAC 5-315-80, prior to said 31st or 61st day, respectively.  In cases where the electric distribution company or energy service provider requests a waiver, a copy of the request for waiver must be mailed simultaneously by the requesting party to the net metering customer and to the commission's Division of Energy Regulation.

C. The electric distribution company shall file with the commission's Division of Energy Regulation a copy of each completed notification form within 30 days of final interconnection.

20 VAC 5-315-40. Conditions of interconnection.

A. A prospective net metering customer may begin operation of his renewable fuel generator on an interconnected basis when:

1. The net metering customer has properly notified both the electric distribution company and energy service provider (in accordance with 20 VAC 5-315-30) of his intent to interconnect;

2. If required by the electric distribution company's net metering tariff, the net metering customer has installed a lockable, electric distribution company accessible, load breaking manual disconnect switch;

3. A licensed electrician has certified, by signing the commission-approved notification form [ as provided in 20 VAC 5-315-90 ], that any required manual disconnect switch has been installed properly and that the renewable fuel generator has been installed in accordance with the manufacturer's specifications as well as all applicable provisions of the National Electrical Code;

4. The vendor has certified, by signing the commission-approved notification form [ as provided in 20 VAC 5-315-90 ], that the renewable fuel generator being installed is in compliance with the requirements established by Underwriters Laboratories or other national testing laboratories in accordance with IEEE Standard 1547, Standard for Interconnecting Distributed Resources with Electric Power Systems, July 2003;

5. In the case of static inverter-connected renewable fuel generators with an alternating current capacity in excess of 10 kilowatts, the net metering customer has had the inverter settings inspected by the electric distribution company.  The inspecting electric distribution company may impose a fee on the net metering customer of no more than $50 for such inspection;

6. In the case of nonstatic inverter-connected renewable fuel generators, the net metering customer has interconnected according to the electric distribution company's interconnection guidelines and the electric distribution company has inspected all protective equipment settings.  The inspecting electric distribution company may impose a fee on the net metering customer of no more than $50 for such inspection.

7. In the case of renewable fuel generators with an alternating current capacity greater than 25 kilowatts, the following requirements shall be met before interconnection may occur:

a. Electric distribution facilities and customer impact limitations.  A renewable fuel generator shall not be permitted to interconnect to distribution facilities if the interconnection would reasonably lead to damage to any of the electric distribution company's facilities or would reasonably lead to voltage regulation or power quality problems at other customer revenue meters due to the incremental effect of the generator on the performance of the electric distribution system, unless the customer reimburses the electric distribution company for its cost to modify any facilities needed to accommodate the interconnection.

b. Secondary, service, and service entrance limitations.  The capacity of the renewable fuel generator shall be less than the capacity of the electric distribution company-owned secondary, service, and service entrance cable connected to the point of interconnection, unless the customer reimburses the electric distribution company for its cost to modify any facilities needed to accommodate the interconnection.

c. Transformer loading limitations.  The renewable fuel generator shall not have the ability to overload the electric distribution company transformer, or any transformer winding, beyond manufacturer or nameplate ratings, unless the customer reimburses the electric distribution company for its cost to modify any facilities needed to accommodate the interconnection.

d. Integration with electric distribution company facilities grounding.  The grounding scheme of the renewable fuel generator shall comply with IEEE 1547, Standard for Interconnecting Distributed Resources with Electric Power Systems, July 2003, and [ shall be consistent with the grounding scheme used by the electric distribution company. If requested by a prospective net metering customer, ] the electric distribution company shall assist the [ prospective ] net metering customer in selecting a grounding scheme that coordinates with its distribution system.

e. Balance limitation.  The renewable fuel generator shall not create a voltage imbalance of more than 3.0% at any other customer's revenue meter if the electric distribution company transformer, with the secondary connected to the point of interconnection, is a three-phase transformer, unless the customer reimburses the electric distribution company for its cost to modify any facilities needed to accommodate the interconnection.

B. A prospective net metering customer shall not be allowed to interconnect a renewable fuel generator if doing so will cause the total rated generating alternating current capacity of all interconnected renewable fuel generators within that customer's electric distribution company's [ Virginia ] service territory to exceed 0.1% of that company's Virginia peak-load forecast for the previous year.  In any case where a prospective net metering customer has submitted a notification form required by 20 VAC 5-315-30 and that customer's interconnection would cause the total rated generating alternating current capacity of all interconnected renewable fuel generators within that electric distribution company's service territory to exceed 0.1% of that company's Virginia peak-load forecast for the previous year, the electric distribution company shall, at the time it becomes aware of the fact, send written notification to such prospective net metering customer and to the commission's Division of Energy Regulation that the interconnection is not allowed.  In addition, upon request from any customer, the electric distribution company shall provide to the customer the amount of capacity still available for interconnection pursuant to § 56-594 D of the Code of Virginia.

C. Neither the electric distribution company nor the energy service provider shall impose any charges upon a net metering customer for any interconnection requirements specified by this chapter, except as provided under subdivisions A 5 and 6 of this section, and 20 VAC 5-315-50 as related to off-site metering.

20 VAC 5-315-90. Commission-approved interconnection notification form. [ Repealed. ]

[ The following commission-approved interconnection notification form shall be used as specified in this chapter.

# Appendix A

# Effective 7/2000 11/2004

# INTERCONNECTION NOTIFICATION 1

PURSUANT TO COMMISSION REGULATION 20 VAC 5-315-30, APPLICANT HEREBY GIVES NOTICE OF INTENT TO OPERATE A GENERATING FACILITY.

### Section 1. Applicant Information

Name:  _______________________________________________________________________

Mail Address:   _________________________________________________________________

City: ________________________  State:  __________     Zip Code:  _____________________

Facility Location  (if different from above):   ___________________________________________

Daytime Phone Number: __________________________________

Distribution Utility:  _____________________  Account Number :  _________________________

Energy Service Provider (ESP):  _________  Account Number : __________________________

(if  different than electric distribution company)

# Proposed Interconnection Date: ____________________________

Section 2. Generating Facility Information

Generator Type (check one):   Solar _______,        Wind  _______,     Hydro  _______________

Generator Manufacturer, Model Name & Number:  ____________________________________

Power Rating in Kilowatts: AC:  ______________  DC: _____________

Inverter Manufacturer, Model Name & Number:  ______________________________________

Battery Backup?  (yes or no)   _______________

Section 3.  Installation Information

Installation Date:_____________________________ Proposed Interconnection Date:  _________________________

Section 3. Information for Renewable Fuel Generators with an Alternating Current Capacity in Excess of

25 Kilowatts

Type (____inverter, ____ induction, ____ synchronous), frequency ______Hz,

number of phases _____,Capacity: DC power ___, AC apparent power _____,

AC real power ___, power factor ___%, AC voltage ___, AC amperage______

Facility schematic and equipment layout must be attached to this form.

Section 4.  Certifications Vendor Certification

1.  The system hardware is listed by Underwriters Laboratories to be in compliance with UL 1741:

Signed (Vendor):  _____________________________________________________________      Date:   ________________

Name (printed):  _________________________________________________________    Company:   __________________

# Phone Number:  ___________________________

Section 5. Electrician Certification

2.  The system has been installed in accordance with the manufacturer's specifications as well as all applicable provisions of the National Electrical Code.

Signed (Licensed Electrician): _________________________   Date: _____________________

# License Number: ___________Phone Number:  ______________________________________

MailAddress:  _________________________________________________________________

City:  ________________________  State:  __________     Zip Code:  ____________________

3.  Utility signature signifies only receipt of this form, in compliance with the Commission's net energy metering

regulations, Regulation 20 VAC 5-315-30.

Signed (Utility Representative):  _________________________      Date:  __________________

I hereby certify that, to the best of my knowledge, all of the information provided in this Notice Notice is true and correct.

Signature of Applicant  ______________________________________________________________

1  Prospective net metering customers considering installing a renewable fuel generator with a capacity in

excess of 25 kilowatts are strongly encouraged to contact his electric distribution company prior to making

financial commitments to the project. ]

DOCUMENT INCORPORATED BY REFERENCE

1547, IEEE Standard for Interconnecting Distributed Resources with Electric Power Systems, July 2003, The Institute of Electrical and Electronics Engineers, Inc.

NOTICE:  The form used in administering 20 VAC 5-315, Regulations Governing Net Energy Metering, is listed and published below.

FORM

Interconnection Notification, Form NMIN, eff. 11/04.

VA.R. Doc. No. R05-105; Filed April 26, 2005, 3:53 p.m.